## Project
Input | General Information |  |  |  | Carbon Free Boston | Whole Building Energy Modelling Calculation Plan
Calculation |  |  |  |  | 259104-00 | Date of last update: 8/28/2017
Notes | [5 empty] | By: Holly Lattin / Ben Brannon
Project Overview |  |  |  | Source/Comments
Project Name | Carbon Free Boston
Project Number | 259104-00
Project Description | Modeling of the building stock for the city of Boston and testing of carbon reduction policies.
Modelling Scope | Prototype models of 15 buildings with conceptual testing of ECMs
Software, Version | EnergyPlus v8.6
Project Start Date | 2017-12-01
Project Completion Date | 2018-08-01
General Data |  |  |  | Source/Comments
Project Vintage | Four vintages to be tested: Pre-1950, 1950-1980, 1980-2000, and post-2000
Principal Building Type | Office
Actual Floor Area (Gross) | 498403
Actual Floor Area (Net) | 498403
Modelled Floor Area (Gross) | #REF!
Modelled Floor Area (Net) | #REF!
Benchmark Site Energy Use Intensity (EUI)
Sustainability Targets | N/A
Codes & Standards |  |  |  | Source/Comments
Applicable Codes & Standards | Varies by vintage.
Energy Code Compliance Path | N/A
Geography |  |  |  | Source/Comments
Project Location | Boston, MA
Weather File | Boston-Logan Airport TMY3
Heating and Cooling Design Conditions | ASHRAE 1%/99%
Site Elevation | 20 ft.
Project Climate Zone(s) | ASHRAE CZ5A
Building Orientation | Varies.
Site Shading | Modeled with no shading.
Model Image
Utility rates |  |  |  | Source/Comments
Electricity Rate/Structure | Varies (Eversource and National Grid)
Natural Gas Rate/Structure | Varies
District Heating Rate/Structure
District Cooling Rate/Structure
Other Utility Rates
Carbon Emission Factors |  |  |  | Source/Comments
Electricity (grid-supplied)
Electricity (grid-displaced)
Natural Gas
Other Carbon Emission Factors
Record of Model Files /Runs
At a minimum, file locations should be documented here for each major project milestone.
| File Name | Description | File Reference Location | Date Created | Created By
1 | Example: Iris 1 | Example: Primary model, backups along the way stored at: | Example: \\global.arup.com\americas\Jobs\S-F\240000\245844-00\4 Internal Project Data\4-04 Calculations\Mech\Energy Modeling\Models | Example: 2/2/2007 | Example: Ben Brannon
2 | Example: Iris 2 | Example: Backup of work progress - Basement Complete | Example: C:\... | Example: 3/6/2008 | Example: Ben Brannon
3 | Example: Iris 3 | Example: Backup of work progress - Bldg A L1 and L2 geometry complete | Example: C:\... | Example: 3/6/2008 | Example: Ben Brannon
4 | Example: Iris 4 | Example: Backup of work progress- Building A Geometry complete | Example: C:\... | Example: 3/9/2008 | Example: Ben Brannon
5 | Example: … | Example: … | Example: … | Example: … | Example: Ben Brannon
6
7
8
9
10
11
12
13
14
15

## Units
Input | Units & Filing Structure |  |  | Carbon Free Boston
Calculation |  |  |  | 259104-00
Notes
Model Units (Auto fills to other tabs) |  | Common Unit Conversions
Opaque Construction U-Value | hr-ft²-F/Btu (R-Value) | Divide | by | To Obtain
Slab-on-Grade U-Value / F-Factor | hr-ft²-F/Btu (R-Value) | Btu/hr-ft²-F | 0.1761 | W/m²-K
Glazing Construction U-Value | Btu/hr-ft²-F (U-Value) | SHGC | 0.87 | SC
Glazing Solar Heat Gain | SHGC | cfm/ft² | 0.19685 | L/s/m²
Infiltration / Air Permeability | (cfm/ft² facade) | ft² | 10.764 | m²
Occupant Density | (ft²/person) | ft | 3.28 | m
Occupant Heat Gain | (Btu/h/person) | Btu/h | 3.412 | W
Lighting & Equipment Heat Gains | (W/ft²) | gal | 0.26417 | liters
Process Loads | (W) | gpm | 15.8504 | L/s
Temperature | (°F) | cfm | 2.1189 | L/s
DHW Demand | (gal/minute) | ft H2O | 2.3067 | psi
Occupant-Based Ventilation | (cfm/person) | ft H2O | 0.33456 | kPa
Area-Based Ventilation | (cfm/ft²) | Pa | 249 | in wg
Air Change Requirement | (ACH) | EER | 3.412 | COP
Area | (ft²) | kW | 3.5169 | tons
Airflow | cfm | Btu/h | 12000 | tons
Water flow | gpm | W | 746 | HP
Heating and Cooling Capacity | kBtu/h | To Obtain | by | Multiply
Temperature Conversion
Recommended Filing Structure [Link] |  | T(°C) = [T(°F) - 32] × 5/9
01 Correspondence Specific to Energy Modelling |  | T(°F) = T(°C) × 9/5 + 32
02 Calculation Plan
03 Input Data
01 Weather Data
02 Zoning Diagram
03 Envelope Data
04 Lighting Data
05 Equipment and Other Internal Gains
06 Service Hot Water
07 Airside System Data
08 Waterside System Data
09 Utility Data
10 Special Systems
11 Equipment Submetering
04 Model Files
05 Results
06 Reference Documents
Opaque Construction Units
Btu/hr-ft²-F (U-Value)
hr-ft²-F/Btu (R-Value)
W/m²-K (U-Value)
m²-K/W (R-Value)
Slab-on-grade Units
Btu/hr-ft²-F (U-Value)
hr-ft²-F/Btu (R-Value)
Btu/hr-ft-F
W/m²-K (U-Value)
m²-K/W (R-Value)
W/m-K
Solar Heat Gain Units
SHGC
SC
G-Value
Infiltration / Air Permeability Units
(cfm/ft² facade)
(L/s/m² facade)
(cfm/ft² floor area)
(L/s/m² floor area)
ACH
(m³/h-m²)
Occupant Density Units
(ft²/person)
(people/1000 ft²)
(m²/person)
(people/100 m²)
(# of people)
Occupant Heat Gain Units
(Btu/h/person)
(W/person)
Internal Gain Units
(W/ft²)
(W/m²)
Process Load Units
(Btu/h)
(W)
(W/ft²)
(W/m²)
Temperature Units
(°F)
(°C)
DHW Demand Units
(gal/person/hour)
(gal/person/day)
(gal/minute)
(L/person/hour)
(L/person/day)
Occupant-Based Ventilation Units
(cfm/person)
(L/s/person)
Area-Based Ventilation Units
(cfm/ft²)
(L/s/m²)
(ACH)
Air-Change Requirements
(cfm)
(L/s)
(ACH)
Area
(ft²)
(m²)
Airflow
cfm
L/s
m³/s
Water Flow
gpm
L/min
Heating and Cooling Capacity
kBtu/h
kW

## Input Summary
Input | Input Summary | [7 empty] | Copy columns as needed for each model variant. Columns that have been superseded may be hidden. |  |  |  |  | Copy columns as needed for each model variant. Columns that have been superseded may be hidden. | Carbon Free Boston
Calculation | [14 empty] | 259104-00
Notes
[10 empty] | CBECS -1950, sample size: 15 | CBECS 1950-1980, sample size: 24 | CBECS 1980-2000, sample size: 14 | CBECS 2000-, sample size: 8
| Pre-1950 |  | 1950-1980 |  | 1980-2000 |  | Post-2000 |  | Source / Comments |  |  |  |  | For Further Discussion
Envelope
| Value | Units | Value | Units | Value | Units | Value | Units
Exterior Wall R-Value | [9 empty] | Wall construction material 13% Aluminum, asbestos, plastic, or wood materials (siding, shingles, tiles, or shakes) 80% Brick, stone, or stucco 7% Concrete block or poured concrete (above grade) Exterior wall replacement 20% Yes Insulation upgrade 40% Yes | Wall construction material 21% Aluminum, asbestos, plastic, or wood materials (siding, shingles, tiles, or shakes) 33% Concrete block or poured concrete (above grade) 42% Brick, stone, or stucco 4% Pre-cast concrete panels Exterior wall replacement 4% Yes Insulation upgrade 17% Yes | Wall construction material 7% Pre-cast concrete panels 29% Brick, stone, or stucco 7% Concrete block or poured concrete (above grade) 14% Sheet metal panels 36% Aluminum, asbestos, plastic, or wood materials (siding, shingles, tiles, or shakes) 7% Decorative or construction glass Exterior wall replacement Insulation upgrade 14% Yes | Wall construction material 12% Concrete block or poured concrete (above grade) 50% Brick, stone, or stucco 38% Aluminum, asbestos, plastic, or wood materials (siding, shingles, tiles, or shakes) Exterior wall replacement Insulation upgrade 12% Yes
Mass Wall | 3.92 | hr-ft²-F/Btu (R-Value) | 6.41 | hr-ft²-F/Btu (R-Value) | 10 | hr-ft²-F/Btu (R-Value) | 8.14 | hr-ft²-F/Btu (R-Value) | - 1950-1980, 1980-2000, and Post-2000 based on DOE reference building models. - Pre-1950: Assume 12' brick walls (R-2.4) with no insulation. Assume 20% have been upgraded to 1980-2000 standard. |  |  |  |  | Assume wood framed (for consistency) for Pre-1950?
Roof R-Value | 11.64 | hr-ft²-F/Btu (R-Value) | 14.2 | hr-ft²-F/Btu (R-Value) | 19.18 | hr-ft²-F/Btu (R-Value) | 16.18 | hr-ft²-F/Btu (R-Value) | - 1950-1980, 1980-2000, and Post-2000 based on DOE reference building models. - Pre-1950: Assume Built-up Roofing 3/8 in. (R-0.33). Assume 60% have been upgraded to 1980-2000 standard. | Roof replacement 60% Yes Roof construction material 40% Plastic, rubber, or synthetic sheeting (single or multiple ply) 7% Slate or tile shingles 20% Built-up (tar, felts, or fiberglass and a ballast, such as stone) 7% Other 27% Asphalt, fiberglass, or other shingles | Roof replacement 42% Yes Roof construction material 38% Plastic, rubber, or synthetic sheeting (single or multiple ply) 21% Built-up (tar, felts, or fiberglass and a ballast, such as stone) 33% Asphalt, fiberglass, or other shingles 8% Slate or tile shingles | Roof replacement 36% Yes Roof construction material 50% Plastic, rubber, or synthetic sheeting (single or multiple ply) 7% Slate or tile shingles 7% Wood shingles, shakes, or other wooden materials 7% Metal surfacing 7% Built-up (tar, felts, or fiberglass and a ballast, such as stone) 21% Asphalt, fiberglass, or other shingles | Roof replacement Roof construction material 38% Plastic, rubber, or synthetic sheeting (single or multiple ply) 12% Built-up (tar, felts, or fiberglass and a ballast, such as stone) 38% Asphalt, fiberglass, or other shingles 12% Metal surfacing
Floor: Slab-on-grade R-Value / F-Factor | 3.05 | hr-ft²-F/Btu (R-Value) | 3.05 | hr-ft²-F/Btu (R-Value) | 3.05 | hr-ft²-F/Btu (R-Value) | 3.05 | hr-ft²-F/Btu (R-Value) | - 1950-1980, 1980-2000, and Post-2000 based on DOE reference building models. - Pre-1950: Assume same as 1950-1980
Underground Walls R-Value | 1.74 | hr-ft²-F/Btu (R-Value) | 1.74 | hr-ft²-F/Btu (R-Value) | 1.74 | hr-ft²-F/Btu (R-Value) | 1.74 | hr-ft²-F/Btu (R-Value) | - 1950-1980, 1980-2000, and Post-2000 based on DOE reference building models. - Pre-1950: Assume same as 1950-1980
Window to Wall Ratio | 38 | % | 38 | % | 38 | % | 38 | % | - 1950-1980, 1980-2000, and Post-2000 based on DOE reference building models. - Pre-1950: Assume same as 1950-1980 | Percent exterior glass 40% 11 to 25 percent 27% 2 to 10 percent 7% 51 to 75 percent 13% 1 percent or less | Percent exterior glass 21% 2 to 10 percent 38% 11 to 25 percent 8% 51 to 75 percent 17% 1 percent or less 8% 26 to 50 percent | Percent exterior glass 29% 2 to 10 percent 43% 11 to 25 percent 7% 51 to 75 percent 7% 1 percent or less 14% 26 to 50 percent | Percent exterior glass 25% 11 to 25 percent 50% 26 to 50 percent 25% 2 to 10 percent | Reduce WWR for pre-2000 vintages?
Glazing Assembly R-Value | [9 empty] | Window replacement 47% Yes Tinted window glass 27% Yes Window glass type 33% Combination of both 47% Multi-layer glass 20% Single layer glass | Window replacement 29% Yes Tinted window glass 50% Yes Window glass type 33% Combination of both 46% Multi-layer glass 21% Single layer glass | Window replacement 7% Yes Tinted window glass 57% Yes Window glass type 14% Combination of both 86% Multi-layer glass | Window replacement Tinted window glass 50% Yes Window glass type 12% Combination of both 75% Multi-layer glass 12% Single layer glass
Windows | 0.62 | Btu/hr-ft²-F (U-Value) | 0.62 | Btu/hr-ft²-F (U-Value) | 0.59 | Btu/hr-ft²-F (U-Value) | 0.57 | Btu/hr-ft²-F (U-Value) | - 1950-1980, 1980-2000, and Post-2000 based on DOE reference building models. - Pre-1950: Assume same as 1950-1980 (based on CBECS glazing type statistics)
Glazing Assembly Solar Heat Gain |  | ffice
Windows | 0.41 | SHGC | 0.41 | SHGC | 0.39 | SHGC | 0.39 | SHGC | - 1950-1980, 1980-2000, and Post-2000 based on DOE reference building models. - Pre-1950: Assume same as 1950-1980 (based on CBECS glazing type statistics)
Glazing Assembly VLT
Windows | 32% | % | 32% | % | 31% | % | 31% | % | - 1950-1980, 1980-2000, and Post-2000 based on DOE reference building models. - Pre-1950: Assume same as 1950-1980 (based on CBECS glazing type statistics)
Skylight to Roof Ratio | N/A | % | N/A | % | N/A | % | N/A | %
Skylight U-Value | N/A | Btu/hr-ft²-F (U-Value) | N/A | Btu/hr-ft²-F (U-Value) | N/A | Btu/hr-ft²-F (U-Value) | N/A | Btu/hr-ft²-F (U-Value)
Skylight Solar Heat Gain | N/A | SHGC | N/A | SHGC | N/A | SHGC | N/A | SHGC
Skylight VLT | N/A | % | N/A | % | N/A | % | N/A | %
Local Shading Devices | None |  | None |  | None |  | None |  |  | External overhangs or awnings 20% Yes | External overhangs or awnings 33% Yes | External overhangs or awnings 7% Yes | External overhangs or awnings 25% Yes
Infiltration / Air Permeability | 2.25 | (cfm/ft² facade) | 1.5 | (cfm/ft² facade) | 1.5 | (cfm/ft² facade) | 0.4 | (cfm/ft² facade) | - 1950-1980, 1980-2000, and Post-2000 based on DOE reference building models. - Pre-1950: Assume 50% increase compared to 1950-1980.
Occupancy
Occupant Density | Space Type | Occupant Density | Space Type | Occupant Density | Space Type | Occupant Density | Space Type | Occupant Density |  | Occupancy (Individual Variables) Number of employees avg: 0.001359906768580741 per sqft | Occupancy (Individual Variables) Number of employees avg: 0.002974018362961516 per sqft | Occupancy (Individual Variables) Number of employees avg: 0.0026351841718186652 per sqft | Occupancy (Individual Variables) Number of employees avg: 0.0022199312714776633 per sqft
|  | (ft²/person) |  | (ft²/person) |  | (ft²/person) |  | (ft²/person)
| Basement | 400 | Basement | 400 | Basement | 400 | Basement | 400 | - 1950-1980, 1980-2000, and Post-2000 based on DOE reference building models. - Pre-1950: Assume same as 1950-1980
| Perimeter | 200 | Perimeter | 200 | Perimeter | 200 | Perimeter | 200
| Core | 200 | Core | 200 | Core | 200 | Core | 200
Lighting & Receptacles
Interior Lighting Power Density | Space Type | Lighting Power Density | Space Type | Lighting Power Density | Space Type | Lighting Power Density | Space Type | Lighting Power Density |  | Lighting type Light-emitting diode (LED) bulbs 27% Yes Incandescent bulbs 53% Yes Fluorescent bulbs 100% Yes High intensity discharge (HID) bulbs 27% Yes Halogen bulbs 40% Yes Compact fluorescent bulbs 67% Yes Lighting upgrade 67% Yes | Lighting type Light-emitting diode (LED) bulbs 25% Yes Incandescent bulbs 46% Yes Fluorescent bulbs 92% Yes High intensity discharge (HID) bulbs 4% Yes Halogen bulbs 29% Yes Compact fluorescent bulbs 79% Yes Lighting upgrade 42% Yes | Lighting type Light-emitting diode (LED) bulbs 36% Yes Incandescent bulbs 50% Yes Fluorescent bulbs 86% Yes Halogen bulbs 43% Yes Compact fluorescent bulbs 57% Yes Lighting upgrade 50% Yes | Lighting type Light-emitting diode (LED) bulbs 25% Yes Incandescent bulbs 38% Yes Fluorescent bulbs 88% Yes High intensity discharge (HID) bulbs 12% Yes Halogen bulbs 12% Yes Compact fluorescent bulbs 62% Yes Lighting upgrade 12% Yes
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²)
| Basement | 1.5 | Basement | 1.5 | Basement | 1.5 | Basement | 1 | - 1950-1980, 1980-2000, and Post-2000 based on DOE reference building models. - Pre-1950: Assume same as 1950-1980 | [5 empty] | Lighting type LED Light-emitting diode (LED) bulbs 25% Yes FLUOR Fluorescent bulbs 92% Yes OTLT Other type of bulbs BULB Incandescent bulbs 46% Yes CFLR Compact fluorescent bulbs 79% Yes HALO Halogen bulbs 29% Yes HID High intensity discharge (HID) bulbs 4% Yes | Lighting type LED Light-emitting diode (LED) bulbs 36% Yes FLUOR Fluorescent bulbs 86% Yes OTLT Other type of bulbs BULB Incandescent bulbs 50% Yes CFLR Compact fluorescent bulbs 57% Yes HALO Halogen bulbs 43% Yes HID High intensity discharge (HID) bulbs | Lighting type LED Light-emitting diode (LED) bulbs 25% Yes FLUOR Fluorescent bulbs 88% Yes OTLT Other type of bulbs BULB Incandescent bulbs 38% Yes CFLR Compact fluorescent bulbs 62% Yes HALO Halogen bulbs 12% Yes HID High intensity discharge (HID) bulbs 12% Yes
| Perimeter | 1 | Perimeter | 1 | Perimeter | 1 | Perimeter | 0.75
| Core | 1 | Core | 1 | Core | 1 | Core | 0.75
Daylighting Controls | None |  | None |  | None |  | None
Other Lighting Control Credits | None |  | None |  | None |  | None |  |  | Lighting controls Multi-level lighting or dimming 20% Yes Occupancy sensors 73% Yes Light scheduling 33% Yes BAS controls lighting 7% Yes | Lighting controls Multi-level lighting or dimming 17% Yes BAS controls lighting 4% Yes Occupancy sensors 50% Yes Light scheduling 29% Yes Daylight harvesting 4% Yes | Lighting controls Multi-level lighting or dimming 14% Yes Occupancy sensors 36% Yes Light scheduling 36% Yes BAS controls lighting 21% Yes | Lighting controls Multi-level lighting or dimming 12% Yes Occupancy sensors 50% Yes Light scheduling 25% Yes | According to CBECS, most offices have occupancy sensors, many have scheduled lighting and a few have dimming. Should we adjust across all vintages?
External / Site Lighting Power (W) | Exterior Lighting | 61595 | Exterior Lighting | 61595 | Exterior Lighting | 61595 | Exterior Lighting | 51262
Receptacle Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density |  | Plug loads (Individual Variables) Number of closed case refrigeration units avg: 1.1744946736666549e-05 per sqft Number of refrigerated vending machines avg: 2.1753011192564054e-05 per sqft Number of walk-in units avg: 1.7543859649122806e-05 per sqft Number of residential refrigerators avg: 3.655976232558446e-05 per sqft Number of computers avg: 0.0012668783204813122 per sqft Number of compact refrigerators avg: 3.36683332491625e-05 per sqft Plug load control 7% Yes Number of open case refrigeration units avg: 5.2631578947368424e-05 per sqft Electrical upgrade 53% Yes | Plug loads (Individual Variables) Number of ice makers avg: 4.426002766251729e-05 per sqft Number of closed case refrigeration units avg: 0.00039468690702087285 per sqft Number of refrigerated vending machines avg: 2.7103331451157537e-05 per sqft Number of walk-in units avg: 2.4439918533604887e-05 per sqft Number of residential refrigerators avg: 8.684930038063582e-05 per sqft Number of computers avg: 0.002981050986520805 per sqft Number of compact refrigerators avg: 9.86252241482367e-05 per sqft Plug load control 8% Yes Electrical upgrade 25% Yes | Plug loads (Individual Variables) Number of ice makers avg: 7.142857142857143e-06 per sqft Number of closed case refrigeration units avg: 1.9178082191780822e-05 per sqft Number of refrigerated vending machines avg: 2.238802628652793e-05 per sqft Number of walk-in units avg: 4.49438202247191e-06 per sqft Number of residential refrigerators avg: 4.919093851132686e-05 per sqft Number of computers avg: 0.0011028964441728995 per sqft Number of compact refrigerators avg: 8.117624377226005e-05 per sqft Electrical upgrade 29% Yes | Plug loads (Individual Variables) Number of ice makers avg: 6.0606060606060605e-05 per sqft Number of closed case refrigeration units avg: 0.00017647058823529413 per sqft Number of refrigerated vending machines avg: 2.898550724637681e-05 per sqft Number of residential refrigerators avg: 0.00010058675607711651 per sqft Number of computers avg: 0.0013998613998614 per sqft Number of compact refrigerators avg: 0.00018867924528301886 per sqft Number of walk-in units avg: 6.0606060606060605e-05 per sqft Number of open case refrigeration units avg: 0.00011764705882352942 per sqft Electrical upgrade 12% Yes
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²)
| Basement | 0.75 | Basement | 0.75 | Basement | 0.75 | Basement | 0.75 | - 1950-1980, 1980-2000, and Post-2000 based on DOE reference building models. - Pre-1950: Assume same as 1950-1980
| Perimeter | 0.75 | Perimeter | 0.75 | Perimeter | 0.75 | Perimeter | 0.75
| Core | 0.75 | Core | 0.75 | Core | 0.75 | Core | 0.75
Process Loads | Process Load Type | Equipment Load | Process Load Type | Equipment Load | Process Load Type | Equipment Load | Process Load Type | Equipment Load |  | Process load (Individual Variables) Elevators 60% Yes Number of servers avg: 5.7171509119241996e-05 per sqft Data center or server farm sqft category Data center or server farm sqft category 13% 500 square feet or less 13% 501 to 1,500 square feet Cooking fuel source Electricity used for cooking 33% Yes Natural gas used for cooking 13% Yes Manufacturing fuel source Electricity used for manufacturing 13% Yes | Cooking fuel source Electricity used for cooking 17% Yes Natural gas used for cooking 21% Yes Process load (Individual Variables) Elevators 33% Yes Number of servers avg: 8.292905419413692e-05 per sqft Data center or server farm sqft category 4% 500 square feet or less Manufacturing fuel source Electricity used for manufacturing 8% Yes | Cooking fuel source Electricity used for cooking 29% Yes Natural gas used for cooking 14% Yes Process load (Individual Variables) Elevators 21% Yes Data center or server farm sqft category Data center or server farm sqft category 7% 1,501 to 3,000 square feet 7% Over 10,000 square feet Number of servers avg: 0.00025734304998303875 per sqft Manufacturing fuel source | Cooking fuel source Electricity used for cooking 25% Yes Natural gas used for cooking 25% Yes Process load (Individual Variables) Elevators 50% Yes Data center or server farm sqft category 12% 500 square feet or less Number of servers avg: 0.00012116316639741518 per sqft Manufacturing fuel source
|  | (W) |  | (W) |  | (W) |  | (W)
| Elevators | 244444 | Elevators | 244444 | Elevators | 244444 | Elevators | 244444 | - 1950-1980, 1980-2000, and Post-2000 based on DOE reference building models. - Pre-1950: Assume same as 1950-1980
Schedules
Internal Gain Schedules | Space Type | Schedule | Space Type | Schedule | Space Type | Schedule | Space Type | Schedule
| Basement | BLDG_OCC_SCH | Basement | BLDG_OCC_SCH | Basement | BLDG_OCC_SCH | Basement | BLDG_OCC_SCH | - 1950-1980, 1980-2000, and Post-2000 based on DOE reference building models. - Pre-1950: Assume same as 1950-1980
| Perimeter | BLDG_OCC_SCH | Perimeter | BLDG_OCC_SCH | Perimeter | BLDG_OCC_SCH | Perimeter | BLDG_OCC_SCH
| Core | BLDG_OCC_SCH | Core | BLDG_OCC_SCH | Core | BLDG_OCC_SCH | Core | BLDG_OCC_SCH
| #REF! | Example: Lobby |  |  |  |  | #REF! | Example: Lobby
| #REF! | Example: Kitchen |  |  |  |  | #REF! | Example: Kitchen
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Kitchen |  |  |  |  | #REF! | Example: Kitchen
| #REF! | Example: Lobby |  |  |  |  | #REF! | Example: Lobby
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
Process Load Schedules | Process Load Type | Schedule | Process Load Type | Schedule | Process Load Type | Schedule | Process Load Type | Schedule
| Elevators | BLDG_ELEVATORS | Elevators | BLDG_ELEVATORS | Elevators | BLDG_ELEVATORS | Elevators | BLDG_ELEVATORS
Building Hours of Operation | Occupied 7 am -10 pm Weekdays, 50% occupied until midnight |  | Occupied 7 am -10 pm Weekdays, 50% occupied until midnight |  | Occupied 7 am -10 pm Weekdays, 50% occupied until midnight |  | Occupied 7 am -10 pm Weekdays, 50% occupied until midnight
HVAC Airside
Primary HVAC System Type - Dominant space type | Packaged central air handling unit with CAV |  | Multizone VAV |  | Multizone VAV |  | Multizone VAV |  | Pre 1950 CBECCS- packaged AHU with AC | Heating ventilation type Heating ventilation: Central air handling with VAV 33% Yes Heating ventilation: Underfloor air distribution 7% Yes Heating ventilation: Dedicated outside air system 7% Yes Heating ventilation: Central air handling with CAV 27% Yes Cooling ventilation type Cooling ventilation: Dedicated outside air system 7% Yes Cooling ventilation: Underfloor air distribution 7% Yes Cooling ventilation: Central air-handling unit with CAV 40% Yes Cooling ventilation: Central air-handling unit with VAV 33% Yes Main heating equipment 20% Packaged central unit (roof mounted) 40% Boilers inside (or adjacent to) the building that produce steam or hot water 13% Heat pumps (other than components of a packaged unit) 13% Furnaces that heat air directly, without using steam or hot water 13% District steam or hot water piped in from outside the building HVAC equipment upgrade 60% Yes | Heating ventilation type Heating ventilation: None of these 4% Yes Heating ventilation: Central air handling with VAV 42% Yes Heating ventilation: Underfloor air distribution 4% Yes Heating ventilation: Demand controlled ventilation 4% Yes Heating ventilation: Dedicated outside air system 4% Yes Heating ventilation: Central air handling with CAV 50% Yes Cooling ventilation type Cooling ventilation: Dedicated outside air system 4% Yes Cooling ventilation: Underfloor air distribution 4% Yes Cooling ventilation: Central air-handling unit with CAV 50% Yes Cooling ventilation: Demand controlled ventilation 4% Yes Cooling ventilation: Central air-handling unit with VAV 29% Yes Main heating equipment 8% Individual space heaters (other than heat pumps) 54% Packaged central unit (roof mounted) 21% Boilers inside (or adjacent to) the building that produce steam or hot water 4% Heat pumps (other than components of a packaged unit) 12% District steam or hot water piped in from outside the building HVAC equipment upgrade 46% Yes | Heating ventilation type Heating ventilation: Central air handling with VAV 29% Yes Heating ventilation: Underfloor air distribution 7% Yes Heating ventilation: Dedicated outside air system 14% Yes Heating ventilation: Central air handling with CAV 29% Yes Cooling ventilation type Cooling ventilation: Dedicated outside air system 14% Yes Cooling ventilation: Underfloor air distribution 14% Yes Cooling ventilation: Central air-handling unit with CAV 36% Yes Cooling ventilation: Central air-handling unit with VAV 36% Yes Main heating equipment 14% Individual space heaters (other than heat pumps) 29% Boilers inside (or adjacent to) the building that produce steam or hot water 50% Packaged central unit (roof mounted) 7% Heat pumps (other than components of a packaged unit) HVAC equipment upgrade 50% Yes | Heating ventilation type Heating ventilation: Central air handling with VAV 62% Yes Heating ventilation: Central air handling with CAV 50% Yes Cooling ventilation type Cooling ventilation: Central air-handling unit with CAV 50% Yes Cooling ventilation: Central air-handling unit with VAV 50% Yes Main heating equipment 12% District steam or hot water piped in from outside the building 25% Boilers inside (or adjacent to) the building that produce steam or hot water 12% Furnaces that heat air directly, without using steam or hot water 38% Packaged central unit (roof mounted) HVAC equipment upgrade | Change system types? CBECS indicate steam/hot water boilers for pre-1950 and packaged central unit for post-1950.
Other HVAC System Type(s) | None |  | None |  | None |  | None
System Parameters and Controls (Economizer, DCV, energy recovery, etc.) | Temperature controlled by programmable thermostat |  | Differential Dry Bulb Economizer |  | Differential Dry Bulb Economizer |  | Differential Dry Bulb Economizer |  | Pre 1950 CBECCS- programmable thermostat | How reduce cooling 27% Manually shut down equipment 7% Manually change thermostat 20% Part of the Building Automation System 40% Programmable thermostat Economizer cycle 47% Yes How reduce heating 20% Manually change thermostat 40% Programmable thermostat 20% Part of the Building Automation System | How reduce cooling 4% Manually change thermostat 29% Part of the Building Automation System 17% Manually shut down equipment 38% Programmable thermostat Economizer cycle 25% Yes How reduce heating 12% Manually change thermostat 33% Part of the Building Automation System 42% Programmable thermostat | How reduce cooling 7% Manually shut down equipment 21% Manually change thermostat 43% Programmable thermostat 21% Part of the Building Automation System Economizer cycle 21% Yes How reduce heating 29% Manually change thermostat 43% Programmable thermostat 14% Part of the Building Automation System | How reduce cooling 12% Manually change thermostat 25% Manually shut down equipment 12% Part of the Building Automation System Economizer cycle 38% Yes How reduce heating 25% Manually change thermostat 12% Programmable thermostat 12% Part of the Building Automation System
HVAC Waterside
Cooling Source Parameters | Direct expansion coils in air handling units, COP = 2.70 |  | 2 Chillers, COP = 5.11 |  | 2 Chillers, COP = 5.2 |  | 2 Chillers, COP = 5.5 |  | Pre 1950 CBECCS- packaged AC, main cooling replaced ASHRAE 90.1 2004- EER = 9.2 for air-cooled AC >760 kBtuh | Main cooling replaced 87% Yes Chiller type Chiller type: Water cooled 7% Yes Chiller type: Air-cooled 7% Yes Cooling fuel source Electricity used for cooling 100% Yes | Main cooling replaced 67% Yes Chiller type Chiller type: Water cooled 17% Yes Chiller type: Air-cooled 4% Yes Cooling fuel source District chilled water used for cooling 4% Yes Electricity used for cooling 92% Yes | Main cooling replaced 64% Yes Chiller type Chiller type: Water cooled 14% Yes Chiller type: Air-cooled 7% Yes Cooling fuel source Electricity used for cooling 100% Yes | Chiller type Chiller type: Air-cooled 12% Yes Cooling fuel source Electricity used for cooling 75% Yes District chilled water used for cooling 12% Yes
Chilled Water Loop & Pump Parameters | N/A (packaged system) |  | Variable speed pump, 90% efficient |  | Variable speed pump, 90% efficient |  | Variable speed pump, 90% efficient
Condenser Water Loop & Pump Parameters | N/A (packaged system) |  | Constant speed pump, 87% efficient |  | Constant speed pump, 87% efficient |  | Constant speed pump, 87% efficient
Cooling tower Parameters | N/A (packaged system) |  | 2 cooling towers |  | 2 cooling towers |  | 2 cooling towers
Heating Source Parameters | Natural gas fired boiler, 78% efficient |  | Gas boiler, 76% efficient |  | Gas boiler, 70% efficient |  | Gas boiler, 78% efficient |  | Pre 1950 CBECCS- natural gas heating, 73% heating system replaced | Heating fuel source District steam used for main heating 13% Yes Fuel oil used for main heating 27% Yes Natural gas used for main heating 40% Yes Electricity used for main heating 20% Yes Main heating replaced 73% Yes | Heating fuel source District steam used for main heating 12% Yes Electricity used for main heating 12% Yes Propane used for main heating 8% Yes Fuel oil used for main heating 21% Yes Natural gas used for main heating 46% Yes Main heating replaced 54% Yes | Heating fuel source Fuel oil used for main heating 21% Yes Natural gas used for main heating 43% Yes Electricity used for main heating 36% Yes Main heating replaced 36% Yes | Heating fuel source Fuel oil used for main heating 25% Yes Natural gas used for main heating 38% Yes District hot water used for main heating 12% Yes Electricity used for main heating 12% Yes | Why is 1980-2000 boiler the least efficient?
Hot Water Loop & Pump Parameters | Steam (no pump) |  | Variable speed pump, 87.5% efficient |  | Variable speed pump, 87.5% efficient |  | Variable speed pump, 87.5% efficient
Service Hot Water
Domestic Hot Water System Parameters | Electric water heater, 95% efficient |  | Gas boiler, 78% efficient, 60C setpoint |  | Gas boiler, 78% efficient, 60C setpoint |  | Gas boiler, 80% efficient, 60C setpoint |  | Pre 1950 CBECCS- electric water heating | DHW fuel source Electricity used for water heating 67% Yes Fuel oil used for water heating 13% Yes District steam used for water heating 7% Yes Natural gas used for water heating 13% Yes Plumbing system upgrade 53% Yes | DHW fuel source Electricity used for water heating 71% Yes District steam used for water heating 8% Yes Propane used for water heating 8% Yes Fuel oil used for water heating 12% Yes Natural gas used for water heating 17% Yes Plumbing system upgrade 21% Yes | Plumbing system upgrade 21% Yes DHW fuel source Electricity used for water heating 71% Yes Fuel oil used for water heating 7% Yes Natural gas used for water heating 21% Yes | Plumbing system upgrade 12% Yes DHW fuel source Electricity used for water heating 50% Yes Fuel oil used for water heating 12% Yes Natural gas used for water heating 38% Yes | Change to electric water heaters for post-1950? (CBECS)
Renewable Energy Systems
Renewable Energy System Description and Parameters | None |  | None |  | None |  | None
General Notes
Notes

## Pre-1950 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/minute) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Basement | Y | Occupied M-F, 7 am to 10 pm | 70 | 72 | 74 | 79 | N/A | N/A | 0 | 25 | 0 | 0 | 0 | N | N/A | Unitary | HotWater | Unitary |  |  |  | 3.5 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.7
Perimeter | Y | Occupied M-F, 7 am to 10 pm | 70 | 72 | 74 | 79 | N/A | N/A | 0 | 25 | 0 | 0 | 0 | N | N/A | Unitary | HotWater | Unitary |  |  |  | 3.5 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.7
Core | Y | Occupied M-F, 7 am to 10 pm | 70 | 72 | 74 | 79 | N/A | N/A | 5 | 25 | 0 | 0 | 0 | N | N/A | Unitary | HotWater | Unitary |  |  |  | 3.5 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.7

## 1950-1980 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/minute) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Basement | Y | Occupied M-F, 7 am to 10 pm | 70 | 72 | 74 | 79 | N/A | N/A | 0 | 25 | 0 | 0 | 0 | N | N/A | VAV | HotWater | VAV | HotWater | WaterCooled | ElectricCentrifugalChiller | 5.11 | NaturalGas | HotWaterBoiler | 0.72 | NaturalGas | 0.72
Perimeter | Y | Occupied M-F, 7 am to 10 pm | 70 | 72 | 74 | 79 | N/A | N/A | 0 | 25 | 0 | 0 | 0 | N | N/A | VAV | HotWater | VAV | HotWater | WaterCooled | ElectricCentrifugalChiller | 5.11 | NaturalGas | HotWaterBoiler | 0.72 | NaturalGas | 0.72
Core | Y | Occupied M-F, 7 am to 10 pm | 70 | 72 | 74 | 79 | N/A | N/A | 5 | 25 | 0 | 0 | 0 | N | N/A | VAV | HotWater | VAV | HotWater | WaterCooled | ElectricCentrifugalChiller | 5.11 | NaturalGas | HotWaterBoiler | 0.72 | NaturalGas | 0.72

## 1980-2000 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/minute) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Basement | Y | Occupied M-F, 7 am to 10 pm | 70 | 72 | 74 | 79 | N/A | N/A | 0 | 25 | 0 | 0 | 0 | N | N/A | VAV | HotWater | VAV | HotWater | WaterCooled | ElectricCentrifugalChiller | 5.2 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.7
Perimeter | Y | Occupied M-F, 7 am to 10 pm | 70 | 72 | 74 | 79 | N/A | N/A | 0 | 25 | 0 | 0 | 0 | N | N/A | VAV | HotWater | VAV | HotWater | WaterCooled | ElectricCentrifugalChiller | 5.2 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.7
Core | Y | Occupied M-F, 7 am to 10 pm | 70 | 72 | 74 | 79 | N/A | N/A | 5 | 25 | 0 | 0 | 0 | N | N/A | VAV | HotWater | VAV | HotWater | WaterCooled | ElectricCentrifugalChiller | 5.2 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.7

## Post-2000 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/minute) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Basement | Y | Occupied M-F, 7 am to 10 pm | 70 | 72 | 74 | 79 | N/A | N/A | 0 | 25 | 0 | 0 | 0 | N | N/A | VAV | HotWater | VAV | HotWater | WaterCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.75 | NaturalGas | 0.8
Perimeter | Y | Occupied M-F, 7 am to 10 pm | 70 | 72 | 74 | 79 | N/A | N/A | 0 | 25 | 0 | 0 | 0 | N | N/A | VAV | HotWater | VAV | HotWater | WaterCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.75 | NaturalGas | 0.8
Core | Y | Occupied M-F, 7 am to 10 pm | 70 | 72 | 74 | 79 | N/A | N/A | 5 | 25 | 0 | 0 | 0 | N | N/A | VAV | HotWater | VAV | HotWater | WaterCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.75 | NaturalGas | 0.8

## Pre-1950 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Office | Office | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Office | Office | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Office | Office | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  | Sun/Holiday | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - Office | Office | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  | Sun/Holiday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Elevator | Elevator | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.2 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | ASHRAE 90.1 Users Manual (update per BU comments)
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## 1950-1980 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Office | Office | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Office | Office | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Office | Office | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  | Sun/Holiday | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - Office | Office | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  | Sun/Holiday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Elevator | Elevator | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.2 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | ASHRAE 90.1 Users Manual (update per BU comments)
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## 1980-2000 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Office | Office | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Office | Office | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Office | Office | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  | Sun/Holiday | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - Office | Office | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  | Sun/Holiday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Elevator | Elevator | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.2 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | ASHRAE 90.1 Users Manual (update per BU comments)
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## Post-2000 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Occupancy | Occupancy | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Lighting | Lighting | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Plug | Plug | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  | Sun/Holiday | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - DHW | DHW | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  | Sun/Holiday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Elevator | Elevator | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.2 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | ASHRAE 90.1 Users Manual (update per BU comments)
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## Review
Input | Review |  |  |  | Carbon Free Boston |  | Notes:
Calculation |  |  |  |  | 259104-00 |  | - Create a copy of the Review tab for each model review
Notes | [6 empty] | - The reviewer should review the model itself, and not rely on what is documented in the Calc Plan
[5 empty] | Modeller | Reviewer
Reviewed by:
Date of review:
Review type:
Project Information (section to be filled out by modeller prior to review)
Project phase & modelling protocol: | Example: 100% Design Development, ASHRAE 90.1-2010 proposed and baseline model
Link to archived model file:
Link to zoning diagram:
Link to relevant drawing set:
Link to current results:
Link to energy model report:
Self-review of model is complete (Column G) |  | If "No", please indicate why self-review has not been performed:
Questions for reviewer and/or comments about model
Model Metrics | Proposed | Baseline | Benchmark (if known) | Units
Energy Use Intensity (EUI) |  |  |  | kBtu/ft²/year
Heating Plant Capacity |  |  |  | Btu/ft²
Cooling Plant Capacity |  |  |  | ft²/ton
Total Design Supply Airflow |  |  |  | cfm/ft²
Total Outdoor Airflow |  |  |  | cfm/ft²
Documentation and file storage
Inputs documented in this workbook or elsewhere
Files archived and saved in appropriate location on network
Detailed calculations (in support of input values) are documented and saved
Comments
Weather
Appropriate and correct weather file is used. A copy is saved on the network in the "Weather Data" folder.
Climate zone is correct for project location
Appropriate and correct Design Day data is used (check against Basis of Design report)
Comments
Geometry and Shading
Building compass orientation is correct
Building elevation above sea level is correct
Overhangs and/or other shading devices, or site shading, if modelled, are correctly configured in the software
Comments
Zoning
The number of zones in the model is appropriate for the desired level of analysis. Rooms of a similar type and internal load density with the same exposure may be zoned together.
Zoning is the same between model variants, unless variation is justified by an evaluated measure
Comments
Envelope and Construction
Window to gross wall ratio seems reasonable for the building and matches design drawings
Construction types are correctly assigned to proposed and baseline models
Window U-values, SHGC/G-values, and VLT are whole-assembly values (including framing impacts) and are input as required by the software
Opaque U-values are whole-assembly values and are input as required by the software. Insulation values of steel or wood-framed walls are appropriately de-rated in accordance with ASHRAE Appendix A or other reference standard.
U-values of horizontal constructions and glazing are derated for horizontal convection (U-values should be worse than vertical assemblies)
For natural ventilation models: window opening sizes, opening positions and the ventilation methodology are correct
Model accounts for an appropriate level of thermal mass. (Check that construction layer build-up reasonably matches design, or room mass settings are appropriate for the building construction type.)
Modelled infiltration rates are reasonable and identical between model variants, unless modification is justified for a measure evaluation
Comments
Internal Loads
Interior lighting power densities are reasonable given the building use(s)
Decorative lighting is accounted for in lighting power density values or separately, as appropriate
Daylight control is included where appropriate
Credit is taken for reduced lighting power due to occupancy sensors where appropriate
Receptacle loads and occupant densities are the same for all model variants, unless modification is justified for a measure evaluation
Peak and scheduled equipment loads represent anticipated actual draws from the equipment rather than nameplate values
Electrical room: entire building switchgear capacity is not assigned as an electric load
Comments
Schedules
Schedules are the same for all model variants, unless modification is justified for a measure evaluation
Internal load schedules set the load to 100% on for the cooling design condition and 100% off for the heating design condition
Internal gain schedules vary throughout the day appropriately
Schedules used are reasonable (i.e. taken from a reference standard, and/or informed by conversation with building owner)
Any continuous loads have an appropriate schedule applied (e.g. escalators, process equipment)
Elevator schedule is included, if applicable
Exterior lighting schedule or photocell control is included, if applicable
Comments
Space Conditioning
All conditioned zones are assigned to HVAC systems
Any included unconditioned zones are set to be unconditioned in the model
Thermostat setpoints and driftpoints are correct
Comments
Airside Systems
Airside systems reasonably approximate the designed systems
Supply air temperatures and control strategies (e.g. SAT reset, economizer control) match the proposed design and baseline requirements
System schedules are consistent with design (e.g. fan schedules align with occupancy schedules such that the HVAC systems are enabled during occupied hours)
Ventilation is included per the design intent. Ventilation rates meet applicable codes.
Ventilation design flow rates and schedules are identical between model variants unless modification is justified
Exhaust is properly accounted for within the capabilities of the software tool. Room exhaust is distinguished from system level exhaust.
Schedules set the ventilation flows to 100% for the heating and cooling design conditions
Ventilation is scheduled ON during occupied hours and OFF during unoccupied hours, or otherwise according to the design sequence of operation
Demand controlled ventilation is modelled if applicable
Proposed fan power is correctly modelled per the design brake horsepowers and motor efficiencies. Baseline fan power includes any applicable pressure drop adjustments. Any included return and exhaust fan power is accounted for.
Fan drives are modelled correctly as either variable or constant speed
Pressure drop across heat recovery devices is accounted for (and not double counted)
Comments
Waterside Systems and Plant Equipment
Equipment types and efficiencies match the proposed design and baseline requirements
Part-load curves are based on actual equipment data or reasonably approximate part-load performance
Capacity of heating and cooling plants is reasonable (check SF/capacity)
Pumps and heat rejection fans are modelled correctly as either variable or constant speed
Control of the plant equipment in the model reasonably approximates the design sequence of operations (e.g. boiler and chiller staging, loop temperatures and reset controls)
If packaged equipment is used, efficiencies of equipment are broken out into supply fan, condenser fan, and compressor
Domestic hot water has been included for both models, as appropriate
Comments
Utility Rates
Rates are included. They are the same for all model variants, unless modification is justified
If Peak and Off-Peak rates apply, they are correctly implemented
Utility rates change often. Documentation of the utility rate(s) used for the analysis has been saved with the model files.
Comments
Metrics Checks
Building predicted annual energy costs are reasonable
Building EUI (Energy Use Index, energy use per square foot) is relatively close to benchmarks for your building type. Refer to the BEM Toolkit for sources of benchmarking data.
Annual cooling and heating load profiles make sense
The HVAC systems effectively satisfy the building loads (i.e. any "unmet" load hours are acceptable for the analysis). If high unmet loads occur, investigate and revise the model to resolve any problems
Comments
Energy Results by End Use
Differences in energy used by end use category between model variants can be explained by actual measures
Fan and pump power differences between model variants are roughly proportional to cooling and heating differences
Correct and consistent units are used when reporting the energy results
Energy uses which should be the same between variant models (e.g. plug loads) are indeed the same
Percentage of energy used by various end uses is reasonable given the building use(s)
Comments
Review Close-Out
Do the results of the energy model make sense according to experiential expertise, engineering judgment, and rules of thumb? If not, review the results again after the modeller has addressed the review comments.
Comments
LEED Specific Review Items
LEED Minimum Energy Performance Calculator is complete and highlighted comments on the Performance Outputs tab have been addressed.
Modelled floor area and space types are consistent with information reported in PIf3: Occupant and Usage Data.
Modelled system parameters align with the mechanical schedules provided for PIf4: Schedule and Overview Documents.
Modelled outdoor airflow is consistent with design OA reported in IEQp1 62.1 Calculator and AHU schedules.
Outdoor air is modelled per the design in the proposed, and per Appendix G requirements in the baseline.
Whenever credit is taken for demand control ventilation in the Proposed Case, the outside air ventilation rates for the Baseline Case are modelled using minimum ASHRAE 62.1 rates.
Any exceptional calculations have been documented in the LEED Minimum Energy Performance Calculator and a supplemental detailed narrative has been provided.
Any LEED CIRs related to the project have been clearly referenced in the documentation.
Core & shell projects: Model follows LEED C&S Appendices guidance. All unfinished spaces are included and modelled identically in the baseline and proposed, unless tenant lease agreement requires improvement over baseline requirements.
Utility rates are sourced from the same place (either EIA rates or actual utility rates for the project).
District energy systems are modelled per the guidance in the reference manual (v4) or the Treatment of District and Campus Thermal Energy In LEED (v2009).
Tilted surfaces are correctly modelled as walls or roofs as defined by ASHRAE 90.1 (per 90.1-2010, roofs are horizontal or tilted at an angle of less than 60° from horizontal).
Answer Options
Yes
No
Unclear
N/A
Review Type
Condensed
Detailed
Note on B10: Condensed reviews are recommended for earlier project phases. Detailed reviews are recommended for later project phases and/or review of a beginner energy modeler's work.