## Project
Input | General Information |  |  |  | Carbon Free Boston | Whole Building Energy Modelling Calculation Plan
Calculation |  |  |  |  | 259104-00 | Date of last update: 8/28/2017
Notes | [5 empty] | By: Holly Lattin / Ben Brannon
Project Overview |  |  |  | Source/Comments
Project Name | Carbon Free Boston
Project Number | 259104-00
Project Description | Modeling of the building stock for the city of Boston and testing of carbon reduction policies.
Modelling Scope | Prototype models of 15 buildings with conceptual testing of ECMs
Software, Version | EnergyPlus v8.6
Project Start Date | 2017-12-01
Project Completion Date | 2018-08-01
General Data |  |  |  | Source/Comments
Project Vintage | Four vintages to be tested: Pre-1950, 1950-1980, 1980-2000, and post-2000
Principal Building Type | Fire-Police
Actual Floor Area (Gross) | 10996.72
Actual Floor Area (Net) | 10996.72
Modelled Floor Area (Gross) | 10996.72
Modelled Floor Area (Net) | 10996.72
Benchmark Site Energy Use Intensity (EUI)
Sustainability Targets | N/A
Codes & Standards |  |  |  | Source/Comments
Applicable Codes & Standards | Varies by vintage.
Energy Code Compliance Path | N/A
Geography |  |  |  | Source/Comments
Project Location | Boston, MA
Weather File | Boston-Logan Airport TMY3
Heating and Cooling Design Conditions | ASHRAE 1%/99%
Site Elevation | 20 ft.
Project Climate Zone(s) | ASHRAE CZ5A
Building Orientation | Varies.
Site Shading | Modeled with no shading.
Model Image
Utility rates |  |  |  | Source/Comments
Electricity Rate/Structure | Varies (Eversource and National Grid)
Natural Gas Rate/Structure | Varies
District Heating Rate/Structure
District Cooling Rate/Structure
Other Utility Rates
Carbon Emission Factors |  |  |  | Source/Comments
Electricity (grid-supplied)
Electricity (grid-displaced)
Natural Gas
Other Carbon Emission Factors
Record of Model Files /Runs
At a minimum, file locations should be documented here for each major project milestone.
| File Name | Description | File Reference Location | Date Created | Created By
1 | Example: Iris 1 | Example: Primary model, backups along the way stored at: | Example: \\global.arup.com\americas\Jobs\S-F\240000\245844-00\4 Internal Project Data\4-04 Calculations\Mech\Energy Modeling\Models | Example: 2/2/2007 | Example: Ben Brannon
2 | Example: Iris 2 | Example: Backup of work progress - Basement Complete | Example: C:\... | Example: 3/6/2008 | Example: Ben Brannon
3 | Example: Iris 3 | Example: Backup of work progress - Bldg A L1 and L2 geometry complete | Example: C:\... | Example: 3/6/2008 | Example: Ben Brannon
4 | Example: Iris 4 | Example: Backup of work progress- Building A Geometry complete | Example: C:\... | Example: 3/9/2008 | Example: Ben Brannon
5 | Example: … | Example: … | Example: … | Example: … | Example: Ben Brannon
6
7
8
9
10
11
12
13
14
15

## Units
Input | Units & Filing Structure |  |  | Carbon Free Boston
Calculation |  |  |  | 259104-00
Notes
Model Units (Auto fills to other tabs) |  | Common Unit Conversions
Opaque Construction U-Value | hr-ft²-F/Btu (R-Value) | Divide | by | To Obtain
Slab-on-Grade U-Value / F-Factor | hr-ft²-F/Btu (R-Value) | Btu/hr-ft²-F | 0.1761 | W/m²-K
Glazing Construction U-Value | Btu/hr-ft²-F (U-Value) | SHGC | 0.87 | SC
Glazing Solar Heat Gain | SHGC | cfm/ft² | 0.19685 | L/s/m²
Infiltration / Air Permeability | ACH | ft² | 10.764 | m²
Occupant Density | (ft²/person) | ft | 3.28 | m
Occupant Heat Gain | (Btu/h/person) | Btu/h | 3.412 | W
Lighting & Equipment Heat Gains | (W/ft²) | gal | 0.26417 | liters
Process Loads | (W) | gpm | 15.8504 | L/s
Temperature | (°F) | cfm | 2.1189 | L/s
DHW Demand | (gal/person/day) | ft H2O | 2.3067 | psi
Occupant-Based Ventilation | (cfm/person) | ft H2O | 0.33456 | kPa
Area-Based Ventilation | (cfm/ft²) | Pa | 249 | in wg
Air Change Requirement | (ACH) | EER | 3.412 | COP
Area | (ft²) | kW | 3.5169 | tons
Airflow | cfm | Btu/h | 12000 | tons
Water flow | gpm | W | 746 | HP
Heating and Cooling Capacity | kBtu/h | To Obtain | by | Multiply
Refrigeration | (W)
Temperature Conversion
Recommended Filing Structure [Link] |  | T(°C) = [T(°F) - 32] × 5/9
01 Correspondence Specific to Energy Modelling |  | T(°F) = T(°C) × 9/5 + 32
02 Calculation Plan
03 Input Data
01 Weather Data
02 Zoning Diagram
03 Envelope Data
04 Lighting Data
05 Equipment and Other Internal Gains
06 Service Hot Water
07 Airside System Data
08 Waterside System Data
09 Utility Data
10 Special Systems
11 Equipment Submetering
04 Model Files
05 Results
06 Reference Documents
Opaque Construction Units
Btu/hr-ft²-F (U-Value)
hr-ft²-F/Btu (R-Value)
W/m²-K (U-Value)
m²-K/W (R-Value)
Slab-on-grade Units
Btu/hr-ft²-F (U-Value)
hr-ft²-F/Btu (R-Value)
Btu/hr-ft-F
W/m²-K (U-Value)
m²-K/W (R-Value)
W/m-K
Solar Heat Gain Units
SHGC
SC
G-Value
Infiltration / Air Permeability Units
(cfm/ft² facade)
(L/s/m² facade)
(cfm/ft² floor area)
(L/s/m² floor area)
ACH
(m³/h-m²)
Occupant Density Units
(ft²/person)
(people/1000 ft²)
(m²/person)
(people/100 m²)
(# of people)
Occupant Heat Gain Units
(Btu/h/person)
(W/person)
Internal Gain Units
(W/ft²)
(W/m²)
Process Load Units
(Btu/h)
(W)
(W/ft²)
(W/m²)
Temperature Units
(°F)
(°C)
DHW Demand Units
(gal/person/hour)
(gal/person/day)
(L/person/hour)
(L/person/day)
Occupant-Based Ventilation Units
(cfm/person)
(L/s/person)
Area-Based Ventilation Units
(cfm/ft²)
(L/s/m²)
(ACH)
Air-Change Requirements
(cfm)
(L/s)
(ACH)
Area
(ft²)
(m²)
Airflow
cfm
L/s
m³/s
Water Flow
gpm
L/min
Heating and Cooling Capacity
kBtu/h
kW

## Input Summary
Input | Input Summary | [7 empty] | Copy columns as needed for each model variant. Columns that have been superseded may be hidden. | Copy columns as needed for each model variant. Columns that have been superseded may be hidden. |  |  |  |  | Copy columns as needed for each model variant. Columns that have been superseded may be hidden. | Carbon Free Boston
Calculation | [15 empty] | 259104-00
Notes
[10 empty] | CBECS -1950 OFFICE | CBECS -1950 sample size: 0 | CBECS 1950-1980, sample size: 2 | CBECS 1980-2000, sample size: 1 | CBECS 2000-, sample size: 4
| Pre-1950 |  | 1950-1980 |  | 1980-2000 |  | Post-2000 |  | Source / Comments | Source / Comments - Detailed |  |  |  |  | For Further Discussion
Envelope
| Value | Units | Value | Units | Value | Units | Value | Units | Pre-1950- No CBECS data available.
Exterior Wall R-Value | [11 empty] | Wall construction material 100% Brick, stone, or stucco Exterior wall replacement Insulation upgrade | Wall construction material 100% Concrete block or poured concrete (above grade) Exterior wall replacement Insulation upgrade | Wall construction material 50% Brick, stone, or stucco 50% Aluminum, asbestos, plastic, or wood materials (siding, shingles, tiles, or shakes) Exterior wall replacement Insulation upgrade | Update based on Office model updates?
Mass Wall | 3.92 | hr-ft²-F/Btu (R-Value) | 6.41 | hr-ft²-F/Btu (R-Value) | 10 | hr-ft²-F/Btu (R-Value) | 8.14 | hr-ft²-F/Btu (R-Value) | Post-1950- Small office DOE reference model Pre-1950s- Assume same as office (Brick wall (R-2.4) with no insulation. 20% have been upgraded to 1980-2000 standard.)
Roof R-Value | 11.454 | hr-ft²-F/Btu (R-Value) | 14.2 | hr-ft²-F/Btu (R-Value) | 18.87 | hr-ft²-F/Btu (R-Value) | 29.7 | hr-ft²-F/Btu (R-Value) | Post-1950- Small office DOE reference model Pre-1950s- Assume same as office (Brick wall (R-2.4) with no insulation. 60% have been upgraded to 1980-2000 standard.) |  |  | Roof replacement Roof construction material 50% Built-up (tar, felts, or fiberglass and a ballast, such as stone) 50% Asphalt, fiberglass, or other shingles | Roof replacement 100% Yes Roof construction material 100% Plastic, rubber, or synthetic sheeting (single or multiple ply) | Roof replacement Roof construction material 25% Plastic, rubber, or synthetic sheeting (single or multiple ply) 50% Asphalt, fiberglass, or other shingles 25% Metal surfacing
Floor: Slab-on-grade R-Value / F-Factor | 3.05 | hr-ft²-F/Btu (R-Value) | 3.05 | hr-ft²-F/Btu (R-Value) | 3.05 | hr-ft²-F/Btu (R-Value) | 3.05 | hr-ft²-F/Btu (R-Value) | Post-1950- Small office DOE reference model Pre-1950s- Assume same as post-1950
Underground Walls R-Value | N/A | hr-ft²-F/Btu (R-Value) | N/A | hr-ft²-F/Btu (R-Value) | N/A | hr-ft²-F/Btu (R-Value) | N/A | hr-ft²-F/Btu (R-Value) | Post-1950- Small office DOE reference model Pre-1950s- Assume same as post-1950
Window to Wall Ratio | 21.2 | % | 21.2 | % | 21.2 | % | 21.2 | % | Post-1950- Small office DOE reference model Pre-1950s- Assume same as post-1950 |  |  | Percent exterior glass 50% 1 percent or less 50% 11 to 25 percent | Percent exterior glass 100% 2 to 10 percent | Percent exterior glass 25% 1 percent or less 75% 2 to 10 percent
Glazing Assembly R-Value | [11 empty] | Window replacement Tinted window glass 50% Yes Window glass type 50% Combination of both 50% Single layer glass | Window replacement 100% Yes Tinted window glass Window glass type 100% Multi-layer glass | Window replacement Tinted window glass 25% Yes Window glass type 100% Multi-layer glass
Hotel Room Windows | 0.62 | Btu/hr-ft²-F (U-Value) | 0.62 | Btu/hr-ft²-F (U-Value) | 0.59 | Btu/hr-ft²-F (U-Value) | 0.57 | Btu/hr-ft²-F (U-Value) | Post-1950- Small office DOE reference model Pre-1950s- Assume same as post-1950
Glazing Assembly Solar Heat Gain
Hotel Room Windows | 0.41 | SHGC | 0.41 | SHGC | 0.39 | SHGC | 0.39 | SHGC | Post-1950- Small office DOE reference model Pre-1950s- Assume same as post-1950
Glazing Assembly VLT
Hotel Room Windows | 32% | % | 32% | % | 31% | % | 31% | % | Post-1950- Small office DOE reference model Pre-1950s- Assume same as post-1950
Skylight to Roof Ratio | N/A | % | N/A | % | N/A | % | N/A | %
Skylight U-Value | N/A | Btu/hr-ft²-F (U-Value) | N/A | Btu/hr-ft²-F (U-Value) | N/A | Btu/hr-ft²-F (U-Value) | N/A | Btu/hr-ft²-F (U-Value)
Skylight Solar Heat Gain | N/A | SHGC | N/A | SHGC | N/A | SHGC | N/A | SHGC
Skylight VLT | N/A | % | N/A | % | N/A | % | N/A | %
Local Shading Devices | N/A |  | N/A |  | N/A |  | N/A |  |  |  |  | External overhangs or awnings | External overhangs or awnings | External overhangs or awnings 25% Yes
Infiltration / Air Permeability | 2.52 | ACH | 1.68 | ACH | 1.68 | ACH | 0.45 | ACH | Post-1950- Small office DOE reference model Pre-1950s- Assume 50% increase compared to 1950-1980.
Occupancy
Occupant Density | Space Type | Occupant Density | Space Type | Occupant Density | Space Type | Occupant Density | Space Type | Occupant Density |  |  |  | Occupancy (Individual Variables) Number of employees avg: 0.003079937304075235 per sqft | Occupancy (Individual Variables) Number of employees avg: 0.002625 per sqft | Occupancy (Individual Variables) Number of employees avg: 0.0009384775808133472 per sqft | CBECS data shows much lower occupancy density
|  | (ft²/person) |  | (ft²/person) |  | (ft²/person) |  | (ft²/person)
| Sleeping Quarters | 33 | Sleeping Quarters | 33 | Sleeping Quarters | 33 | Sleeping Quarters | 33 | COMNET Appendix B: Fire Station Sleeping Quarters
| Office Core | 33 | Office Core | 33 | Office Core | 33 | Office Core | 33 | COMNET Appendix B, Police/Fire Station
| Office Perimeter | 33 | Office Perimeter | 33 | Office Perimeter | 33 | Office Perimeter | 33 | COMNET Appendix B, Police/Fire Station
| Vehicle Storage | 500 | Vehicle Storage | 500 | Vehicle Storage | 500 | Vehicle Storage | 500
Lighting & Receptacles
Interior Lighting Power Density | Space Type | Lighting Power Density | Space Type | Lighting Power Density | Space Type | Lighting Power Density | Space Type | Lighting Power Density |  |  |  | Lighting type Incandescent bulbs 50% Yes Fluorescent bulbs 100% Yes Halogen bulbs 50% Yes Compact fluorescent bulbs 100% Yes Lighting upgrade | Lighting type Light-emitting diode (LED) bulbs 100% Yes Fluorescent bulbs 100% Yes Halogen bulbs 100% Yes Compact fluorescent bulbs 100% Yes Lighting upgrade 100% Yes | Lighting type Incandescent bulbs 25% Yes Fluorescent bulbs 100% Yes High intensity discharge (HID) bulbs 50% Yes Compact fluorescent bulbs 25% Yes Lighting upgrade
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²)
| Sleeping Quarters | 1 | Sleeping Quarters | 1 | Sleeping Quarters | 1.5 | Sleeping Quarters | 1.1 | COMNET Appendix B: Fire Station Sleeping Quarters | [5 empty] | Confirm that lighting increases 80% between post-2000s and Pre-2000. (Not enough CBECS data available.)
| Office Core | 1 | Office Core | 1 | Office Core | 1.6 | Office Core | 1.3 | COMNET Appendix B, Police/Fire Station
| Office Perimeter | 1 | Office Perimeter | 1 | Office Perimeter | 1.6 | Office Perimeter | 1.3 | COMNET Appendix B, Police/Fire Station
| Vehicle Storage | 0.25 | Vehicle Storage | 0.25 | Vehicle Storage | 0.4 | Vehicle Storage | 0.3 | COMNET Appendix B, Parking Garage
Daylighting Controls | N/A |  | N/A |  | N/A |  | N/A
Other Lighting Control Credits | N/A |  | N/A |  | N/A |  | N/A |  |  |  |  | Lighting controls Occupancy sensors 50% Yes Light scheduling 50% Yes | Lighting controls | Lighting controls Occupancy sensors 25% Yes Light scheduling 25% Yes BAS controls lighting 25% Yes | Add lighting controls?
External / Site Lighting Power (W) | Exterior Lights | 2766 | Exterior Lights | 2766 | Exterior Lights | 2766 | Exterior Lights | 2303
Receptacle Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density |  |  |  | Plug loads (Individual Variables) Number of ice makers avg: 8.47457627118644e-06 per sqft Number of closed case refrigeration units avg: 2.5423728813559322e-05 per sqft Number of refrigerated vending machines avg: 3.134796238244514e-05 per sqft Number of walk-in units avg: 1.694915254237288e-05 per sqft Number of computers avg: 0.001959247648902821 per sqft Number of compact refrigerators avg: 3.918495297805643e-05 per sqft Plug load control 50% Yes Electrical upgrade | Plug loads (Individual Variables) Number of computers avg: 0.00175 per sqft Number of residential refrigerators avg: 0.00025 per sqft Electrical upgrade 100% Yes | Plug loads (Individual Variables) Number of computers avg: 0.00044365572315882877 per sqft Number of refrigerated vending machines avg: 9.75609756097561e-05 per sqft Number of residential refrigerators avg: 0.0001160541586073501 per sqft Electrical upgrade
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²)
| Sleeping Quarters | 0.1 | Sleeping Quarters | 0.1 | Sleeping Quarters | 0.25 | Sleeping Quarters | 0.25 | COMNET Appendix B: Fire Station Sleeping Quarters
| Office Core | 0.5 | Office Core | 0.5 | Office Core | 1 | Office Core | 1 | COMNET Appendix B, Police/Fire Station
| Office Perimeter | 0.5 | Office Perimeter | 0.5 | Office Perimeter | 1 | Office Perimeter | 1 | COMNET Appendix B, Police/Fire Station
| Vehicle Storage | 0.1 | Vehicle Storage | 0.1 | Vehicle Storage | 0.25 | Vehicle Storage | 0.25 | COMNET Appendix B, Police/Fire Station
Gas Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²)
| Sleeping Quarters | 0.99 | Sleeping Quarters | 0.99 | Sleeping Quarters | 0.99 | Sleeping Quarters | 0.99 | COMNET Appendix B, Police/Fire Station Concentrated in One Zone
| Office Core | 0 | Office Core | 0 | Office Core | 0 | Office Core | 0
| Office Perimeter | 0 | Office Perimeter | 0 | Office Perimeter | 0 | Office Perimeter | 0
| Vehicle Storage | 0 | Vehicle Storage | 0 | Vehicle Storage | 0 | Vehicle Storage | 0
Process Loads | Process Load Type | Equipment Load | Process Load Type | Equipment Load | Process Load Type | Equipment Load | Process Load Type | Equipment Load |  |  |  | Cooking fuel source Electricity used for cooking 50% Yes Process load (Individual Variables) Elevators 50% Yes Data center or server farm sqft category 50% 500 square feet or less Number of servers avg: 0.00013322884012539185 per sqft Manufacturing fuel source | Cooking fuel source Propane used for cooking 100% Yes Process load (Individual Variables) Number of servers avg: 0.0005 per sqft Manufacturing fuel source | Cooking fuel source Electricity used for cooking 25% Yes Natural gas used for cooking 25% Yes Process load (Individual Variables) Number of servers avg: 0 per sqft Manufacturing fuel source
|  | (W) |  | (W) |  | (W) |  | (W)
| N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Refrigeration
Cases | Space, Case | Cooling Capacity | Space, Case | Cooling Capacity | Space, Case | Cooling Capacity | Space, Case | Cooling Capacity | [6 empty] | Where do these assumptions come from?
|  | (W) |  | (W) |  | (W) |  | (W)
| Freezer | 183.3361 | Freezer | 183.3361 | Freezer | 183.3361 | Freezer | 183.3361
| Open Case | 366.6721 | Open Case | 366.6721 | Open Case | 366.6721 | Open Case | 366.6721
Condenser | Condenser Name | Equipment Load | Condenser Name | Equipment Load | Condenser Name | Equipment Load | Condenser Name | Equipment Load
|  | (W) |  | (W) |  | (W) |  | (W)
| Rack 1 | 40 | Rack 1 | 40 | Rack 1 | 40 | Rack 1 | 40
| Rack 2 | 80 | Rack 2 | 80 | Rack 2 | 80 | Rack 2 | 80
Schedules
Internal Gain Schedules | Space Type | Schedule | Space Type | Schedule | Space Type | Schedule | Space Type | Schedule
| Sleeping Quarters | C-12 Residential | Sleeping Quarters | C-12 Residential | Sleeping Quarters | C-12 Residential | Sleeping Quarters | C-12 Residential | COMNET Appendix C Schedules
| Office Core | C-2 Public | Office Core | C-2 Public | Office Core | C-2 Public | Office Core | C-2 Public | COMNET Appendix C Schedules
| Office Perimeter | C-2 Public | Office Perimeter | C-2 Public | Office Perimeter | C-2 Public | Office Perimeter | C-2 Public | COMNET Appendix C Schedules
| Vehicle Storage | C-6 Parking Garage | Vehicle Storage | C-6 Parking Garage | Vehicle Storage | C-6 Parking Garage | Vehicle Storage | C-6 Parking Garage | COMNET Appendix C Schedules
| #REF! | Example: Lobby |  |  |  |  | #REF! | Example: Lobby
| #REF! | Example: Kitchen |  |  |  |  | #REF! | Example: Kitchen
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Kitchen |  |  |  |  | #REF! | Example: Kitchen
| #REF! | Example: Lobby |  |  |  |  | #REF! | Example: Lobby
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
Process Load Schedules | Process Load Type | Schedule | Process Load Type | Schedule | Process Load Type | Schedule | Process Load Type | Schedule
| N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Building Hours of Operation | 24/7 Operation |  | 24/7 Operation |  | 24/7 Operation |  | 24/7 Operation
HVAC Airside
Primary HVAC System Type - Dominant space type | Packaged central air handling unit with CAV |  | Packaged single zone air conditioning with unitary cooling coils and gas heating coils |  | Packaged single zone air conditioning with unitary cooling coils and gas heating coils |  | Packaged single zone air conditioning with unitary cooling coils and gas heating coils |  | Post 1950s - DOE reference model for office Pre 1950s - CBECS data for office | HVAC equipment upgrade 60% Yes Cooling ventilation type CLVFLR Cooling ventilation: Underfloor air distribution 7% Yes CLVOAS Cooling ventilation: Dedicated outside air system 7% Yes CLVVAV Cooling ventilation: Central air-handling unit with VAV 33% Yes CLVCAV Cooling ventilation: Central air-handling unit with CAV 40% Yes CLVDEM Cooling ventilation: Demand controlled ventilation Main cooling equipment 7% Central chillers inside (or adjacent to) the building that chill water for air conditioning 7% Residential-type central air conditioners (other than heat pumps) that cool air directly and circulate it without using chilled water 60% Packaged air conditioning units (other than heat pumps) 20% Individual room air conditioners (other than heat pumps) 7% Heat pumps for cooling Heating ventilation type HTVFLR Heating ventilation: Underfloor air distribution 7% Yes HTVCAV Heating ventilation: Central air handling with CAV 27% Yes HTVOAS Heating ventilation: Dedicated outside air system 7% Yes HTVVAV Heating ventilation: Central air handling with VAV 33% Yes Main heating equipment 20% Packaged central unit (roof mounted) 13% Furnaces that heat air directly, without using steam or hot water 40% Boilers inside (or adjacent to) the building that produce steam or hot water 13% Heat pumps (other than components of a packaged unit) 13% District steam or hot water piped in from outside the building |  | Heating ventilation type Heating ventilation: Central air handling with VAV 50% Yes Heating ventilation: Central air handling with CAV 50% Yes Cooling ventilation type Cooling ventilation: Central air-handling unit with CAV 50% Yes Cooling ventilation: Central air-handling unit with VAV 50% Yes Main heating equipment 50% Furnaces that heat air directly, without using steam or hot water 50% Boilers inside (or adjacent to) the building that produce steam or hot water HVAC equipment upgrade | Heating ventilation type Heating ventilation: Dedicated outside air system 100% Yes Cooling ventilation type Cooling ventilation: Dedicated outside air system 100% Yes Main heating equipment 100% Boilers inside (or adjacent to) the building that produce steam or hot water HVAC equipment upgrade 100% Yes | Heating ventilation type Heating ventilation: None of these 25% Yes Heating ventilation: Central air handling with VAV 25% Yes Heating ventilation: Central air handling with CAV 25% Yes Cooling ventilation type Cooling ventilation: Central air-handling unit with CAV 25% Yes Cooling ventilation: Central air-handling unit with VAV 25% Yes Main heating equipment 75% Boilers inside (or adjacent to) the building that produce steam or hot water 25% District steam or hot water piped in from outside the building HVAC equipment upgrade | Change system types? CBECS data shows mainly central airhandlers and steam/hot water boilers.
Other HVAC System Type(s) | N/A |  | N/A |  | N/A |  | N/A |  | Post 1950s - DOE reference model for office Pre 1950s - CBECS data for office
System Parameters and Controls (Economizer, DCV, energy recovery, etc.) | Temperature controlled by programmable thermostat |  | No Economizers |  | No Economizers |  | No Economizers |  | Post 1950s - DOE reference model for office Pre 1950s - CBECS data for office | How reduce cooling 20% Part of the Building Automation System 40% Programmable thermostat 27% Manually shut down equipment 7% Manually change thermostat How reduce heating 20% Part of the Building Automation System 40% Programmable thermostat 20% Manually change thermostat Economizer cycle 47% Yes |  | How reduce cooling 50% Part of the Building Automation System Economizer cycle How reduce heating 50% Part of the Building Automation System | How reduce cooling 100% Manually change thermostat Economizer cycle How reduce heating 100% Programmable thermostat | Economizer cycle 50% Yes | Pre-1950 controller inconsistent with other vintages. Review CBECS control data for all vintages.
HVAC Waterside
Cooling Source Parameters | Direct expansion coils in air handling units, COP = 2.70 |  | Unitary cooling coils with COP = 3.38 |  | Unitary cooling coils with COP = 3.07 |  | Unitary cooling coils with COP = 3.67 |  | Post 1950s - DOE reference model for office Pre 1950s - CBECS data for office | Cooling fuel source ELCOOL Electricity used for cooling 100% Yes Chiller type CHLAIRCL Chiller type: Air-cooled 7% Yes CHLWTRCL Chiller type: Water cooled 7% Yes Main cooling replaced 87% Yes |  | Main cooling replaced 50% Yes Chiller type Chiller type: Air-cooled 50% Yes Cooling fuel source Electricity used for cooling 100% Yes | Main cooling replaced 100% Yes Cooling fuel source Electricity used for cooling 100% Yes | Cooling fuel source District chilled water used for cooling 25% Yes Electricity used for cooling 50% Yes
Chilled Water Loop & Pump Parameters | N/A (packaged system) |  | N/A |  | N/A |  | N/A |  | Post 1950s - DOE reference model for office Pre 1950s - CBECS data for office
Condenser Water Loop & Pump Parameters | N/A (packaged system) |  | N/A |  | N/A |  | N/A |  | Post 1950s - DOE reference model for office Pre 1950s - CBECS data for office
Cooling tower Parameters | N/A (packaged system) |  | N/A |  | N/A |  | N/A |  | Post 1950s - DOE reference model for office Pre 1950s - CBECS data for office
Heating Source Parameters | Natural gas fired boiler, 78% efficient |  | Gas heating coils with 78% efficiency |  | Gas heating coils with 80% efficiency |  | Gas heating coils with 80% efficiency |  | Post 1950s - DOE reference model for office Pre 1950s - CBECS data for office | Heating fuel source NGHT1 Natural gas used for main heating 40% Yes ELHT1 Electricity used for main heating 20% Yes SOHT1 Solar used for main heating FKHT1 Fuel oil used for main heating 27% Yes STHT1 District steam used for main heating 13% Yes Main heating equipment 20% Packaged central unit (roof mounted) 13% Furnaces that heat air directly, without using steam or hot water 40% Boilers inside (or adjacent to) the building that produce steam or hot water 13% Heat pumps (other than components of a packaged unit) 13% District steam or hot water piped in from outside the building Main heating replaced 73% Yes |  | Heating fuel source Natural gas used for main heating 100% Yes Main heating replaced 100% Yes | Heating fuel source Wood used for main heating 100% Yes Main heating replaced 100% Yes | Heating fuel source Propane used for main heating 25% Yes Fuel oil used for main heating 25% Yes Natural gas used for main heating 25% Yes District hot water used for main heating 25% Yes | Mix of fuels for post-2000 (CBECS)
Hot Water Loop & Pump Parameters | Steam (no pump) |  | N/A |  | N/A |  | N/A |  | Post 1950s - DOE reference model for office Pre 1950s - CBECS data for office
Service Hot Water
Domestic Hot Water System Parameters | Electric water heater, 95% efficient |  | Natural gas water heater with 78% efficiency |  | Natural gas water heater with 78% efficiency |  | Natural gas water heater with 80% efficiency |  | Post 1950s - DOE reference model for office Pre 1950s - CBECS data for office | DHW fuel source NGWATR Natural gas used for water heating 13% Yes FKWATR Fuel oil used for water heating 13% Yes STWATR District steam used for water heating 7% Yes ELWATR Electricity used for water heating 67% Yes Plumbing system upgrade 53% Yes |  | Plumbing system upgrade DHW fuel source Electricity used for water heating 50% Yes Natural gas used for water heating 50% Yes | DHW fuel source Electricity used for water heating 100% Yes Wood used for water heating 100% Yes Plumbing system upgrade | Plumbing system upgrade DHW fuel source Propane used for water heating 25% Yes Fuel oil used for water heating 25% Yes Natural gas used for water heating 50% Yes | Mix of fuels (CBECS)
Renewable Energy Systems
Renewable Energy System Description and Parameters | N/A |  | N/A |  | N/A |  | N/A
General Notes
Notes

## Pre-1950 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/person/day) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Sleeping Quarters | Y | Setpoint active 24/7 | 67 | 70 | 78 | 82 | N/A | N/A | 33.4 | 20 | 0.21 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary |  |  |  | 2.5 | NaturalGas | HotWaterBoiler | 0.74 | NaturalGas | 0.78 | CBECS 2004 Residential Hot Water Consmption
Office Core | Y | Setpoint active 24/7 | 67 | 70 | 78 | 82 | N/A | N/A | 8.9 | 20 | 0.21 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary |  |  |  | 2.5 | NaturalGas | HotWaterBoiler | 0.74 | NaturalGas | 0.78 | CBECS 2004 Small Office Water Consumption
Office Perimeter | Y | Setpoint active 24/7 | 67 | 70 | 78 | 82 | N/A | N/A | 0 | 20 | 0.21 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary |  |  |  | 2.5 | NaturalGas | HotWaterBoiler | 0.74 | NaturalGas | 0.78
Vehicle Storage | Y | Setpoint active 8 am to 12 am | 60 | 60 | 85 | 90 | N/A | N/A | N/A | 15 | 0.21 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary |  |  |  | 2.5 | NaturalGas | HotWaterBoiler | 0.74 | NaturalGas | 0.78

## 1950-1980 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/person/day) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Sleeping Quarters | Y | Setpoint active 24/7 | 67 | 70 | 78 | 82 | N/A | N/A | 33.4 | 20 | 0.21 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary |  |  |  | 2.5 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78 | CBECS 2004 Residential Hot Water Consmption
Office Core | Y | Setpoint active 24/7 | 67 | 70 | 78 | 82 | N/A | N/A | 8.9 | 20 | 0.21 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary |  |  |  | 2.5 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78 | CBECS 2004 Small Office Water Consumption
Office Perimeter | Y | Setpoint active 24/7 | 67 | 70 | 78 | 82 | N/A | N/A | 0 | 20 | 0.21 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary |  |  |  | 2.5 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78
Vehicle Storage | Y | Setpoint active 8 am to 12 am | 60 | 60 | 85 | 90 | N/A | N/A | N/A | 15 | 0.21 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary |  |  |  | 2.5 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78

## 1980-2000 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/person/day) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Sleeping Quarters | Y | Setpoint active 24/7 | 67 | 70 | 76 | 80 | N/A | N/A | 33.4 | 20 | 0.21 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary |  |  |  | 2.5 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.78 | CBECS 2004 Residential Hot Water Consmption
Office Core | Y | Setpoint active 24/7 | 67 | 70 | 76 | 80 | N/A | N/A | 8.9 | 20 | 0.21 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary |  |  |  | 2.5 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.78 | CBECS 2004 Small Office Water Consumption
Office Perimeter | Y | Setpoint active 24/7 | 67 | 70 | 76 | 80 | N/A | N/A | 0 | 20 | 0.21 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary |  |  |  | 2.5 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.78
Vehicle Storage | Y | Setpoint active 8 am to 12 am | 60 | 60 | 85 | 90 | N/A | N/A | N/A | 15 | 0.21 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary |  |  |  | 2.5 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.78

## Post-2000 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/person/day) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Sleeping Quarters | Y | Setpoint active 24/7 | 67 | 70 | 74 | 74 | N/A | N/A | 33.4 | 20 | 0.21 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary |  |  |  | 3.2 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8 | CBECS 2004 Residential Hot Water Consmption
Office Core | Y | Setpoint active 24/7 | 67 | 70 | 74 | 74 | N/A | N/A | 8.9 | 20 | 0.21 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary |  |  |  | 3.2 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8 | CBECS 2004 Small Office Water Consumption
Office Perimeter | Y | Setpoint active 24/7 | 67 | 70 | 74 | 74 | N/A | N/A | 0 | 20 | 0.21 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary |  |  |  | 3.2 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8
Vehicle Storage | Y | Setpoint active 8 am to 12 am | 60 | 60 | 80 | 85 | N/A | N/A | N/A | N/A | 0.21 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary |  |  |  | 3.2 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8

## Pre-1950 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Sleeping Quarters | Sleeping Quarters | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | COMNET Appendix C
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1
Occupancy - Office Core | Office Core | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | COMNET Appendix C
|  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Occupancy - Garage | Garage | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | Modified COMNET Appendix C
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Occupancy - Office Perimeter | Office Perimeter | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | COMNET Appendix C
|  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Sleeping Quarters | Sleeping Quarters | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.8 | 1 | 1 | 0.7 | 0.4 | 0.2 | COMNET Appendix C
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.8 | 1 | 1 | 0.7 | 0.4 | 0.2
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.8 | 1 | 1 | 0.7 | 0.4 | 0.2
Lighting - Office Core | Office Core | Weekday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | COMNET Appendix C
|  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | Sun/Holiday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Lighting - Garage | Garage | Weekday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | COMNET Appendix C
|  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | Sun/Holiday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Lighting - Office Perimeter | Office Perimeter | Weekday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | COMNET Appendix C
|  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | Sun/Holiday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Sleeping Quarters | Sleeping Quarters | Weekday | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6 | COMNET Appendix C
|  | Sat | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
|  | Sun/Holiday | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
Receptacles - Office Core | Office Core | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | COMNET Appendix C
|  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Receptacles - Garage | Garage | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | COMNET Appendix C
|  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Receptacles - Office Perimeter | Office Perimeter | Weekday | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
|  | Sat | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
|  | Sun/Holiday | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - Sleeping Quarters | Sleeping Quarters | Weekday | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05 | COMNET Appendix C
|  | Sat | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05
|  | Sun/Holiday | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05
Domestic Hot Water - Office Core | Office Core | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.15 | 0.15 | 0.15 | COMNET Appendix C
|  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  | Sun/Holiday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Domestic Hot Water - Garage | Garage | Weekday
Sat
Sun/Holiday
Domestic Hot Water - Office Perimeter | Office Perimeter | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.15 | 0.15 | 0.15 | COMNET Appendix C
|  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  | Sun/Holiday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Sleeping Quarters | Sleeping Quarters | Weekday
Sat
Sun/Holiday
Process Loads - Office Core | Office Core | Weekday
Sat
Sun/Holiday
Process Loads - Garage | Garage | Weekday
Sat
Sun/Holiday
Process Loads - Office Perimeter | Office Perimeter | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## 1950-1980 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Sleeping Quarters | Sleeping Quarters | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | COMNET Appendix C
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1
Occupancy - Office Core | Office Core | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | COMNET Appendix C
|  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Occupancy - Garage | Garage | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | Modified COMNET Appendix C
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Occupancy - Office Perimeter | Office Perimeter | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | COMNET Appendix C
|  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Sleeping Quarters | Sleeping Quarters | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.8 | 1 | 1 | 0.7 | 0.4 | 0.2 | COMNET Appendix C
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.8 | 1 | 1 | 0.7 | 0.4 | 0.2
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.8 | 1 | 1 | 0.7 | 0.4 | 0.2
Lighting - Office Core | Office Core | Weekday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | COMNET Appendix C
|  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | Sun/Holiday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Lighting - Garage | Garage | Weekday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | COMNET Appendix C
|  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | Sun/Holiday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Lighting - Office Perimeter | Office Perimeter | Weekday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | COMNET Appendix C
|  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | Sun/Holiday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Sleeping Quarters | Sleeping Quarters | Weekday | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6 | COMNET Appendix C
|  | Sat | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
|  | Sun/Holiday | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
Receptacles - Office Core | Office Core | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | COMNET Appendix C
|  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Receptacles - Garage | Garage | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | COMNET Appendix C
|  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Receptacles - Office Perimeter | Office Perimeter | Weekday | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
|  | Sat | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
|  | Sun/Holiday | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - Sleeping Quarters | Sleeping Quarters | Weekday | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05 | COMNET Appendix C
|  | Sat | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05
|  | Sun/Holiday | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05
Domestic Hot Water - Office Core | Office Core | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.15 | 0.15 | 0.15 | COMNET Appendix C
|  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  | Sun/Holiday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Domestic Hot Water - Garage | Garage | Weekday
Sat
Sun/Holiday
Domestic Hot Water - Office Perimeter | Office Perimeter | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.15 | 0.15 | 0.15 | COMNET Appendix C
|  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  | Sun/Holiday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Sleeping Quarters | Sleeping Quarters | Weekday
Sat
Sun/Holiday
Process Loads - Office Core | Office Core | Weekday
Sat
Sun/Holiday
Process Loads - Garage | Garage | Weekday
Sat
Sun/Holiday
Process Loads - Office Perimeter | Office Perimeter | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## 1980-2000 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Sleeping Quarters | Sleeping Quarters | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | COMNET Appendix C
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1
Occupancy - Office Core | Office Core | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | COMNET Appendix C
|  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Occupancy - Garage | Garage | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | Modified COMNET Appendix C
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Occupancy - Office Perimeter | Office Perimeter | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | COMNET Appendix C
|  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Sleeping Quarters | Sleeping Quarters | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.8 | 1 | 1 | 0.7 | 0.4 | 0.2 | COMNET Appendix C
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.8 | 1 | 1 | 0.7 | 0.4 | 0.2
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.8 | 1 | 1 | 0.7 | 0.4 | 0.2
Lighting - Office Core | Office Core | Weekday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | COMNET Appendix C
|  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | Sun/Holiday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Lighting - Garage | Garage | Weekday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | COMNET Appendix C
|  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | Sun/Holiday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Lighting - Office Perimeter | Office Perimeter | Weekday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | COMNET Appendix C
|  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | Sun/Holiday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Sleeping Quarters | Sleeping Quarters | Weekday | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6 | COMNET Appendix C
|  | Sat | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
|  | Sun/Holiday | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
Receptacles - Office Core | Office Core | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | COMNET Appendix C
|  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Receptacles - Garage | Garage | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | COMNET Appendix C
|  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Receptacles - Office Perimeter | Office Perimeter | Weekday | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
|  | Sat | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
|  | Sun/Holiday | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - Sleeping Quarters | Sleeping Quarters | Weekday | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05 | COMNET Appendix C
|  | Sat | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05
|  | Sun/Holiday | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05
Domestic Hot Water - Office Core | Office Core | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.15 | 0.15 | 0.15 | COMNET Appendix C
|  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  | Sun/Holiday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Domestic Hot Water - Garage | Garage | Weekday
Sat
Sun/Holiday
Domestic Hot Water - Office Perimeter | Office Perimeter | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.15 | 0.15 | 0.15 | COMNET Appendix C
|  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  | Sun/Holiday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Sleeping Quarters | Sleeping Quarters | Weekday
Sat
Sun/Holiday
Process Loads - Office Core | Office Core | Weekday
Sat
Sun/Holiday
Process Loads - Garage | Garage | Weekday
Sat
Sun/Holiday
Process Loads - Office Perimeter | Office Perimeter | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## Post-2000 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Sleeping Quarters | Sleeping Quarters | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | COMNET Appendix C
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1
Occupancy - Office Core | Office Core | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | COMNET Appendix C
|  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Occupancy - Garage | Garage | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | Modified COMNET Appendix C
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Occupancy - Office Perimeter | Office Perimeter | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | COMNET Appendix C
|  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Sleeping Quarters | Sleeping Quarters | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.8 | 1 | 1 | 0.7 | 0.4 | 0.2 | COMNET Appendix C
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.8 | 1 | 1 | 0.7 | 0.4 | 0.2
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.8 | 1 | 1 | 0.7 | 0.4 | 0.2
Lighting - Office Core | Office Core | Weekday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | COMNET Appendix C
|  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | Sun/Holiday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Lighting - Garage | Garage | Weekday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | COMNET Appendix C
|  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | Sun/Holiday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Lighting - Office Perimeter | Office Perimeter | Weekday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | COMNET Appendix C
|  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | Sun/Holiday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Sleeping Quarters | Sleeping Quarters | Weekday | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6 | COMNET Appendix C
|  | Sat | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
|  | Sun/Holiday | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
Receptacles - Office Core | Office Core | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | COMNET Appendix C
|  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Receptacles - Garage | Garage | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | COMNET Appendix C
|  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Receptacles - Office Perimeter | Office Perimeter | Weekday | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
|  | Sat | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
|  | Sun/Holiday | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - Sleeping Quarters | Sleeping Quarters | Weekday | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05 | COMNET Appendix C
|  | Sat | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05
|  | Sun/Holiday | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05
Domestic Hot Water - Office Core | Office Core | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.15 | 0.15 | 0.15 | COMNET Appendix C
|  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  | Sun/Holiday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Domestic Hot Water - Garage | Garage | Weekday
Sat
Sun/Holiday
Domestic Hot Water - Office Perimeter | Office Perimeter | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.15 | 0.15 | 0.15 | COMNET Appendix C
|  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  | Sun/Holiday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Sleeping Quarters | Sleeping Quarters | Weekday
Sat
Sun/Holiday
Process Loads - Office Core | Office Core | Weekday
Sat
Sun/Holiday
Process Loads - Garage | Garage | Weekday
Sat
Sun/Holiday
Process Loads - Office Perimeter | Office Perimeter | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## Review
Input | Review |  |  |  | Carbon Free Boston |  | Notes:
Calculation |  |  |  |  | 259104-00 |  | - Create a copy of the Review tab for each model review
Notes | [6 empty] | - The reviewer should review the model itself, and not rely on what is documented in the Calc Plan
[5 empty] | Modeller | Reviewer
Reviewed by:
Date of review:
Review type:
Project Information (section to be filled out by modeller prior to review)
Project phase & modelling protocol: | Example: 100% Design Development, ASHRAE 90.1-2010 proposed and baseline model
Link to archived model file:
Link to zoning diagram:
Link to relevant drawing set:
Link to current results:
Link to energy model report:
Self-review of model is complete (Column G) |  | If "No", please indicate why self-review has not been performed:
Questions for reviewer and/or comments about model
Model Metrics | Proposed | Baseline | Benchmark (if known) | Units
Energy Use Intensity (EUI) |  |  |  | kBtu/ft²/year
Heating Plant Capacity |  |  |  | Btu/ft²
Cooling Plant Capacity |  |  |  | ft²/ton
Total Design Supply Airflow |  |  |  | cfm/ft²
Total Outdoor Airflow |  |  |  | cfm/ft²
Documentation and file storage
Inputs documented in this workbook or elsewhere
Files archived and saved in appropriate location on network
Detailed calculations (in support of input values) are documented and saved
Comments
Weather
Appropriate and correct weather file is used. A copy is saved on the network in the "Weather Data" folder.
Climate zone is correct for project location
Appropriate and correct Design Day data is used (check against Basis of Design report)
Comments
Geometry and Shading
Building compass orientation is correct
Building elevation above sea level is correct
Overhangs and/or other shading devices, or site shading, if modelled, are correctly configured in the software
Comments
Zoning
The number of zones in the model is appropriate for the desired level of analysis. Rooms of a similar type and internal load density with the same exposure may be zoned together.
Zoning is the same between model variants, unless variation is justified by an evaluated measure
Comments
Envelope and Construction
Window to gross wall ratio seems reasonable for the building and matches design drawings
Construction types are correctly assigned to proposed and baseline models
Window U-values, SHGC/G-values, and VLT are whole-assembly values (including framing impacts) and are input as required by the software
Opaque U-values are whole-assembly values and are input as required by the software. Insulation values of steel or wood-framed walls are appropriately de-rated in accordance with ASHRAE Appendix A or other reference standard.
U-values of horizontal constructions and glazing are derated for horizontal convection (U-values should be worse than vertical assemblies)
For natural ventilation models: window opening sizes, opening positions and the ventilation methodology are correct
Model accounts for an appropriate level of thermal mass. (Check that construction layer build-up reasonably matches design, or room mass settings are appropriate for the building construction type.)
Modelled infiltration rates are reasonable and identical between model variants, unless modification is justified for a measure evaluation
Comments
Internal Loads
Interior lighting power densities are reasonable given the building use(s)
Decorative lighting is accounted for in lighting power density values or separately, as appropriate
Daylight control is included where appropriate
Credit is taken for reduced lighting power due to occupancy sensors where appropriate
Receptacle loads and occupant densities are the same for all model variants, unless modification is justified for a measure evaluation
Peak and scheduled equipment loads represent anticipated actual draws from the equipment rather than nameplate values
Electrical room: entire building switchgear capacity is not assigned as an electric load
Comments
Schedules
Schedules are the same for all model variants, unless modification is justified for a measure evaluation
Internal load schedules set the load to 100% on for the cooling design condition and 100% off for the heating design condition
Internal gain schedules vary throughout the day appropriately
Schedules used are reasonable (i.e. taken from a reference standard, and/or informed by conversation with building owner)
Any continuous loads have an appropriate schedule applied (e.g. escalators, process equipment)
Elevator schedule is included, if applicable
Exterior lighting schedule or photocell control is included, if applicable
Comments
Space Conditioning
All conditioned zones are assigned to HVAC systems
Any included unconditioned zones are set to be unconditioned in the model
Thermostat setpoints and driftpoints are correct
Comments
Airside Systems
Airside systems reasonably approximate the designed systems
Supply air temperatures and control strategies (e.g. SAT reset, economizer control) match the proposed design and baseline requirements
System schedules are consistent with design (e.g. fan schedules align with occupancy schedules such that the HVAC systems are enabled during occupied hours)
Ventilation is included per the design intent. Ventilation rates meet applicable codes.
Ventilation design flow rates and schedules are identical between model variants unless modification is justified
Exhaust is properly accounted for within the capabilities of the software tool. Room exhaust is distinguished from system level exhaust.
Schedules set the ventilation flows to 100% for the heating and cooling design conditions
Ventilation is scheduled ON during occupied hours and OFF during unoccupied hours, or otherwise according to the design sequence of operation
Demand controlled ventilation is modelled if applicable
Proposed fan power is correctly modelled per the design brake horsepowers and motor efficiencies. Baseline fan power includes any applicable pressure drop adjustments. Any included return and exhaust fan power is accounted for.
Fan drives are modelled correctly as either variable or constant speed
Pressure drop across heat recovery devices is accounted for (and not double counted)
Comments
Waterside Systems and Plant Equipment
Equipment types and efficiencies match the proposed design and baseline requirements
Part-load curves are based on actual equipment data or reasonably approximate part-load performance
Capacity of heating and cooling plants is reasonable (check SF/capacity)
Pumps and heat rejection fans are modelled correctly as either variable or constant speed
Control of the plant equipment in the model reasonably approximates the design sequence of operations (e.g. boiler and chiller staging, loop temperatures and reset controls)
If packaged equipment is used, efficiencies of equipment are broken out into supply fan, condenser fan, and compressor
Domestic hot water has been included for both models, as appropriate
Comments
Utility Rates
Rates are included. They are the same for all model variants, unless modification is justified
If Peak and Off-Peak rates apply, they are correctly implemented
Utility rates change often. Documentation of the utility rate(s) used for the analysis has been saved with the model files.
Comments
Metrics Checks
Building predicted annual energy costs are reasonable
Building EUI (Energy Use Index, energy use per square foot) is relatively close to benchmarks for your building type. Refer to the BEM Toolkit for sources of benchmarking data.
Annual cooling and heating load profiles make sense
The HVAC systems effectively satisfy the building loads (i.e. any "unmet" load hours are acceptable for the analysis). If high unmet loads occur, investigate and revise the model to resolve any problems
Comments
Energy Results by End Use
Differences in energy used by end use category between model variants can be explained by actual measures
Fan and pump power differences between model variants are roughly proportional to cooling and heating differences
Correct and consistent units are used when reporting the energy results
Energy uses which should be the same between variant models (e.g. plug loads) are indeed the same
Percentage of energy used by various end uses is reasonable given the building use(s)
Comments
Review Close-Out
Do the results of the energy model make sense according to experiential expertise, engineering judgment, and rules of thumb? If not, review the results again after the modeller has addressed the review comments.
Comments
LEED Specific Review Items
LEED Minimum Energy Performance Calculator is complete and highlighted comments on the Performance Outputs tab have been addressed.
Modelled floor area and space types are consistent with information reported in PIf3: Occupant and Usage Data.
Modelled system parameters align with the mechanical schedules provided for PIf4: Schedule and Overview Documents.
Modelled outdoor airflow is consistent with design OA reported in IEQp1 62.1 Calculator and AHU schedules.
Outdoor air is modelled per the design in the proposed, and per Appendix G requirements in the baseline.
Whenever credit is taken for demand control ventilation in the Proposed Case, the outside air ventilation rates for the Baseline Case are modelled using minimum ASHRAE 62.1 rates.
Any exceptional calculations have been documented in the LEED Minimum Energy Performance Calculator and a supplemental detailed narrative has been provided.
Any LEED CIRs related to the project have been clearly referenced in the documentation.
Core & shell projects: Model follows LEED C&S Appendices guidance. All unfinished spaces are included and modelled identically in the baseline and proposed, unless tenant lease agreement requires improvement over baseline requirements.
Utility rates are sourced from the same place (either EIA rates or actual utility rates for the project).
District energy systems are modelled per the guidance in the reference manual (v4) or the Treatment of District and Campus Thermal Energy In LEED (v2009).
Tilted surfaces are correctly modelled as walls or roofs as defined by ASHRAE 90.1 (per 90.1-2010, roofs are horizontal or tilted at an angle of less than 60° from horizontal).
Answer Options
Yes
No
Unclear
N/A
Review Type
Condensed
Detailed
Note on B10: Condensed reviews are recommended for earlier project phases. Detailed reviews are recommended for later project phases and/or review of a beginner energy modeler's work.