## Project
Input | General Information |  |  |  | Carbon Free Boston | Whole Building Energy Modelling Calculation Plan
Calculation |  |  |  |  | 259104-00 | Date of last update: 8/28/2017
Notes | [5 empty] | By: Holly Lattin / Ben Brannon
Project Overview |  |  |  | Source/Comments
Project Name | Carbon Free Boston
Project Number | 259104-00
Project Description | Modeling of the building stock for the city of Boston and testing of carbon reduction policies.
Modelling Scope | Prototype models of 15 buildings with conceptual testing of ECMs
Software, Version | EnergyPlus v8.6
Project Start Date | 2017-12-01
Project Completion Date | 2018-08-01
General Data |  |  |  | Source/Comments
Project Vintage | Four vintages to be tested: Pre-1950, 1950-1980, 1980-2000, and post-2000
Principal Building Type | Supermarket
Actual Floor Area (Gross) | 44987
Actual Floor Area (Net) | 44987
Modelled Floor Area (Gross) | 44987
Modelled Floor Area (Net) | 44987
Benchmark Site Energy Use Intensity (EUI)
Sustainability Targets | N/A
Codes & Standards |  |  |  | Source/Comments
Applicable Codes & Standards | Varies by vintage.
Energy Code Compliance Path | N/A
Geography |  |  |  | Source/Comments
Project Location | Boston, MA
Weather File | Boston-Logan Airport TMY3
Heating and Cooling Design Conditions | ASHRAE 1%/99%
Site Elevation | 20 ft.
Project Climate Zone(s) | ASHRAE CZ5A
Building Orientation | Varies.
Site Shading | Modeled with no shading.
Model Image
Utility rates |  |  |  | Source/Comments
Electricity Rate/Structure | Varies (Eversource and National Grid)
Natural Gas Rate/Structure | Varies
District Heating Rate/Structure
District Cooling Rate/Structure
Other Utility Rates
Carbon Emission Factors |  |  |  | Source/Comments
Electricity (grid-supplied)
Electricity (grid-displaced)
Natural Gas
Other Carbon Emission Factors
Record of Model Files /Runs
At a minimum, file locations should be documented here for each major project milestone.
| File Name | Description | File Reference Location | Date Created | Created By
1 | Example: Iris 1 | Example: Primary model, backups along the way stored at: | Example: \\global.arup.com\americas\Jobs\S-F\240000\245844-00\4 Internal Project Data\4-04 Calculations\Mech\Energy Modeling\Models | Example: 2/2/2007 | Example: Ben Brannon
2 | Example: Iris 2 | Example: Backup of work progress - Basement Complete | Example: C:\... | Example: 3/6/2008 | Example: Ben Brannon
3 | Example: Iris 3 | Example: Backup of work progress - Bldg A L1 and L2 geometry complete | Example: C:\... | Example: 3/6/2008 | Example: Ben Brannon
4 | Example: Iris 4 | Example: Backup of work progress- Building A Geometry complete | Example: C:\... | Example: 3/9/2008 | Example: Ben Brannon
5 | Example: … | Example: … | Example: … | Example: … | Example: Ben Brannon
6
7
8
9
10
11
12
13
14
15

## Units
Input | Units & Filing Structure |  |  | Carbon Free Boston
Calculation |  |  |  | 259104-00
Notes
Model Units (Auto fills to other tabs) |  | Common Unit Conversions
Opaque Construction U-Value | hr-ft²-F/Btu (R-Value) | Divide | by | To Obtain
Slab-on-Grade U-Value / F-Factor | hr-ft²-F/Btu (R-Value) | Btu/hr-ft²-F | 0.1761 | W/m²-K
Glazing Construction U-Value | Btu/hr-ft²-F (U-Value) | SHGC | 0.87 | SC
Glazing Solar Heat Gain | SHGC | cfm/ft² | 0.19685 | L/s/m²
Infiltration / Air Permeability | ACH | ft² | 10.764 | m²
Occupant Density | (ft²/person) | ft | 3.28 | m
Occupant Heat Gain | (Btu/h/person) | Btu/h | 3.412 | W
Lighting & Equipment Heat Gains | (W/ft²) | gal | 0.26417 | liters
Process Loads | (W) | gpm | 15.8504 | L/s
Temperature | (°F) | cfm | 2.1189 | L/s
DHW Demand | (gal/person/day) | ft H2O | 2.3067 | psi
Occupant-Based Ventilation | (cfm/person) | ft H2O | 0.33456 | kPa
Area-Based Ventilation | (cfm/ft²) | Pa | 249 | in wg
Air Change Requirement | (ACH) | EER | 3.412 | COP
Area | (ft²) | kW | 3.5169 | tons
Airflow | cfm | Btu/h | 12000 | tons
Water flow | gpm | W | 746 | HP
Heating and Cooling Capacity | kBtu/h | To Obtain | by | Multiply
Refrigeration | (W)
Temperature Conversion
Recommended Filing Structure [Link] |  | T(°C) = [T(°F) - 32] × 5/9
01 Correspondence Specific to Energy Modelling |  | T(°F) = T(°C) × 9/5 + 32
02 Calculation Plan
03 Input Data
01 Weather Data
02 Zoning Diagram
03 Envelope Data
04 Lighting Data
05 Equipment and Other Internal Gains
06 Service Hot Water
07 Airside System Data
08 Waterside System Data
09 Utility Data
10 Special Systems
11 Equipment Submetering
04 Model Files
05 Results
06 Reference Documents
Opaque Construction Units
Btu/hr-ft²-F (U-Value)
hr-ft²-F/Btu (R-Value)
W/m²-K (U-Value)
m²-K/W (R-Value)
Slab-on-grade Units
Btu/hr-ft²-F (U-Value)
hr-ft²-F/Btu (R-Value)
Btu/hr-ft-F
W/m²-K (U-Value)
m²-K/W (R-Value)
W/m-K
Solar Heat Gain Units
SHGC
SC
G-Value
Infiltration / Air Permeability Units
(cfm/ft² facade)
(L/s/m² facade)
(cfm/ft² floor area)
(L/s/m² floor area)
ACH
(m³/h-m²)
Occupant Density Units
(ft²/person)
(people/1000 ft²)
(m²/person)
(people/100 m²)
(# of people)
Occupant Heat Gain Units
(Btu/h/person)
(W/person)
Internal Gain Units
(W/ft²)
(W/m²)
Process Load Units
(Btu/h)
(W)
(W/ft²)
(W/m²)
Temperature Units
(°F)
(°C)
DHW Demand Units
(gal/person/hour)
(gal/person/day)
(L/person/hour)
(L/person/day)
Occupant-Based Ventilation Units
(cfm/person)
(L/s/person)
Area-Based Ventilation Units
(cfm/ft²)
(L/s/m²)
(ACH)
Air-Change Requirements
(cfm)
(L/s)
(ACH)
Area
(ft²)
(m²)
Airflow
cfm
L/s
m³/s
Water Flow
gpm
L/min
Heating and Cooling Capacity
kBtu/h
kW

## Input Summary
Input | Input Summary | [7 empty] | Copy columns as needed for each model variant. Columns that have been superseded may be hidden. |  |  |  |  | Copy columns as needed for each model variant. Columns that have been superseded may be hidden. | Carbon Free Boston
Calculation | [14 empty] | 259104-00
Notes
[10 empty] | CBECS -1950, sample size: 2 | CBECS 1950-1980, sample size: 2 | CBECS 1980-2000, sample size: 1 | CBECS 2000-, sample size: 3
| Pre-1950 |  | 1950-1980 |  | 1980-2000 |  | Post-2000 |  | Source / Comments |  |  |  |  | For Further Discussion
Envelope
| Value | Units | Value | Units | Value | Units | Value | Units
Exterior Wall R-Value | [9 empty] | Wall construction material 100% Aluminum, asbestos, plastic, or wood materials (siding, shingles, tiles, or shakes) Exterior wall replacement Insulation upgrade 50% Yes | Wall construction material 50% Brick, stone, or stucco 50% Aluminum, asbestos, plastic, or wood materials (siding, shingles, tiles, or shakes) Exterior wall replacement Insulation upgrade | Wall construction material 100% Brick, stone, or stucco Exterior wall replacement Insulation upgrade | Wall construction material 33% Brick, stone, or stucco 67% Aluminum, asbestos, plastic, or wood materials (siding, shingles, tiles, or shakes) Exterior wall replacement Insulation upgrade
Mass Wall | 5 | hr-ft²-F/Btu (R-Value) | 7.5 | hr-ft²-F/Btu (R-Value) | 9.5 | hr-ft²-F/Btu (R-Value) | 9.5 | hr-ft²-F/Btu (R-Value) | Post-1950- DOE reference model. Pre-1950: Assume wood framing with no insulation (R-3.8). Assume 0% have been upgraded.
Roof R-Value | 10 | hr-ft²-F/Btu (R-Value) | 15 | hr-ft²-F/Btu (R-Value) | 18 | hr-ft²-F/Btu (R-Value) | 18 | hr-ft²-F/Btu (R-Value) | Post-1950- DOE reference model Pre-1950s- Assume Wood Framing (R-2.46) with no insulation. Assume 50% has been upgraded to 1980-2000 standard. (CBECS) | Roof replacement 50% Yes Roof construction material 50% Asphalt, fiberglass, or other shingles 50% Metal surfacing | Roof replacement Roof construction material 50% Wood shingles, shakes, or other wooden materials 50% Metal surfacing | Roof replacement Roof construction material 100% Plastic, rubber, or synthetic sheeting (single or multiple ply) | Roof construction material 33% Plastic, rubber, or synthetic sheeting (single or multiple ply) 67% Asphalt, fiberglass, or other shingles Roof replacement
Floor: Slab-on-grade R-Value / F-Factor | 1.82 | hr-ft²-F/Btu (R-Value) | 1.82 | hr-ft²-F/Btu (R-Value) | 1.82 | hr-ft²-F/Btu (R-Value) | 1.82 | hr-ft²-F/Btu (R-Value) | Post-1950- DOE reference model Pre-1950s- assume same as post-1950
Underground Walls R-Value | N/A | hr-ft²-F/Btu (R-Value) | N/A | hr-ft²-F/Btu (R-Value) | N/A | hr-ft²-F/Btu (R-Value) | N/A | hr-ft²-F/Btu (R-Value)
Window to Wall Ratio | 10.9 | % | 10.9 | % | 10.9 | % | 10.9 | % | Post-1950- DOE reference model Pre-1950s- assume same as post-1950 (aligns with CBECS data). | Percent exterior glass 50% 11 to 25 percent 50% 2 to 10 percent | Percent exterior glass 50% 1 percent or less | Percent exterior glass 100% 2 to 10 percent | Percent exterior glass 100% 2 to 10 percent
Glazing Assembly R-Value | [9 empty] | Window replacement Tinted window glass Window glass type 100% Single layer glass | Window replacement Tinted window glass Window glass type 50% Single layer glass 50% Multi-layer glass | Window replacement Tinted window glass Window glass type 100% Combination of both | Window replacement Tinted window glass Window glass type 33% Single layer glass 67% Multi-layer glass
Windows | 1.23 | Btu/hr-ft²-F (U-Value) | 0.62 | Btu/hr-ft²-F (U-Value) | 0.59 | Btu/hr-ft²-F (U-Value) | 0.57 | Btu/hr-ft²-F (U-Value) | Post-1950- DOE reference model Pre-1950s- Assuming historic rolled steel sash with single glazing (U-1.3, according to ASHRAE HANDBOOK 1977 Fundamentals). 100% single pane windows and 0% of the windows have been replaced based on CBECS statistics. |  |  |  |  | Should the Pre-1950 glazing performance be this much worse than Post-1950?
Glazing Assembly Solar Heat Gain
Windows | 0.8 | SHGC | 0.41 | SHGC | 0.39 | SHGC | 0.39 | SHGC | Post-1950- DOE reference model Pre-1950: SHGC 0.8 (http://www.energy.ca.gov/title24/archive/2001standards/residential_manual/res_manual_form_s.PDF ) |  |  |  |  | Should the Pre-1950 glazing performance be this much worse than Post-1950?
Glazing Assembly VLT
Windows | 70% | % | 32% | % | 31% | % | 31% | % | Post-1950- DOE reference model Pre-1950s- VLT 70% (https://tyvekbku.com/reading/SG_WindowTechnologies_EnergyImpact.pdf)
Skylight to Roof Ratio | N/A | % | N/A | % | N/A | % | N/A | %
Skylight U-Value | N/A | Btu/hr-ft²-F (U-Value) | N/A | Btu/hr-ft²-F (U-Value) | N/A | Btu/hr-ft²-F (U-Value) | N/A | Btu/hr-ft²-F (U-Value)
Skylight Solar Heat Gain | N/A | SHGC | N/A | SHGC | N/A | SHGC | N/A | SHGC
Skylight VLT | N/A | % | N/A | % | N/A | % | N/A | %
Local Shading Devices | N/A |  | N/A |  | N/A |  | N/A |  |  | External overhangs or awnings 50% Yes | External overhangs or awnings | External overhangs or awnings | External overhangs or awnings
Infiltration / Air Permeability | 1.395 | ACH | 0.93 | ACH | 0.93 | ACH | 0.25 | ACH | Post-1950- DOE reference model Pre-1950s- Assume 50% increase compared to 1950-1980.
Occupancy
Occupant Density | Space Type | Occupant Density | Space Type | Occupant Density | Space Type | Occupant Density | Space Type | Occupant Density |  | Occupancy (Individual Variables) Number of employees avg: 0.0001639344262295082 per sqft | Occupancy (Individual Variables) Number of employees avg: 0.00029304029304029304 per sqft | Occupancy (Individual Variables) Number of employees avg: 0.0010638297872340426 per sqft | Occupancy (Individual Variables) Number of employees avg: 0.0007834101382488479 per sqft
|  | (ft²/person) |  | (ft²/person) |  | (ft²/person) |  | (ft²/person) | Post 1950s- DOE reference model Pre-1950s- no data, assume same as post-1950
| Office | 200 | Office | 200 | Office | 200 | Office | 200
| DryStorage | 300 | DryStorage | 300 | DryStorage | 300 | DryStorage | 300
| Deli | 125 | Deli | 125 | Deli | 125 | Deli | 125
| Sales | 125 | Sales | 125 | Sales | 125 | Sales | 125
| Produce | 125 | Produce | 125 | Produce | 125 | Produce | 125
| Bakery | 125 | Bakery | 125 | Bakery | 125 | Bakery | 125
Lighting & Receptacles
Interior Lighting Power Density | Space Type | Lighting Power Density | Space Type | Lighting Power Density | Space Type | Lighting Power Density | Space Type | Lighting Power Density |  | Lighting type Incandescent bulbs 100% Yes Fluorescent bulbs 100% Yes Lighting upgrade 50% Yes | Lighting type Incandescent bulbs 50% Yes Fluorescent bulbs 100% Yes Halogen bulbs 50% Yes Compact fluorescent bulbs 50% Yes Lighting upgrade | Lighting type Incandescent bulbs 100% Yes Fluorescent bulbs 100% Yes Halogen bulbs 100% Yes Compact fluorescent bulbs 100% Yes Lighting upgrade | Lighting type Light-emitting diode (LED) bulbs 33% Yes Fluorescent bulbs 100% Yes High intensity discharge (HID) bulbs 33% Yes Halogen bulbs 33% Yes Compact fluorescent bulbs 33% Yes Lighting upgrade 33% Yes
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²) | Post 1950s- DOE reference model Pre-1950s- according to CBECS, stores have fluorescent and incandescent lights; 50% of stores have been upgraded. Assume 30% increase in LPD
| Office | 1 | Office | 1 | Office | 1 | Office | 1.1
| DryStorage | 1.11 | DryStorage | 1.11 | DryStorage | 1.11 | DryStorage | 0.8
| Deli | 1 | Deli | 1 | Deli | 1 | Deli | 1
| Sales | 1 | Sales | 1 | Sales | 1 | Sales | 0.75
| Produce | 1 | Produce | 1 | Produce | 1 | Produce | 1
| Bakery | 1 | Bakery | 1 | Bakery | 1 | Bakery | 1
Daylighting Controls | None |  | None |  | None |  | None
Other Lighting Control Credits | None |  | None |  | None |  | None |  |  | Lighting controls | Lighting controls | Lighting controls | Lighting controls Multi-level lighting or dimming 33% Yes Occupancy sensors 33% Yes Light scheduling 33% Yes BAS controls lighting 33% Yes | Add some lighting control (CBECS)?
External / Site Lighting Power (W) | Exterior Lighting | 16402 | Exterior Lighting | 16402 | Exterior Lighting | 16402 | Exterior Lighting | 13577 | Post 1950s- DOE reference model Pre-1950s- no data, assume same as 1950-1980
Receptacle Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Post 1950s- DOE reference model Pre-1950s- no data, assume same as post-1950 | Plug loads (Individual Variables) Number of closed case refrigeration units avg: 0.0005737704918032787 per sqft Number of walk-in units avg: 0.000576923076923077 per sqft Number of residential refrigerators avg: 0.0003278688524590164 per sqft Number of computers avg: 0 per sqft Number of open case refrigeration units avg: 0.0003846153846153846 per sqft Electrical upgrade | Plug loads (Individual Variables) Number of closed case refrigeration units avg: 0.0003663003663003663 per sqft Number of refrigerated vending machines avg: 0.0002926829268292683 per sqft Number of walk-in units avg: 0.0002941176470588235 per sqft Number of residential refrigerators avg: 0.00043956043956043956 per sqft Number of computers avg: 0.00021978021978021978 per sqft Electrical upgrade | Plug loads (Individual Variables) Number of computers avg: 0.000851063829787234 per sqft Number of walk-in units avg: 0.0002127659574468085 per sqft Number of closed case refrigeration units avg: 0.0010638297872340426 per sqft Electrical upgrade | Plug loads (Individual Variables) Number of ice makers avg: 8.241758241758242e-05 per sqft Number of closed case refrigeration units avg: 0.0005529953917050691 per sqft Number of refrigerated vending machines avg: 0.00011764705882352942 per sqft Number of residential refrigerators avg: 0.00010989010989010989 per sqft Number of computers avg: 0.0005299539170506912 per sqft Number of walk-in units avg: 0.00029953917050691244 per sqft Number of open case refrigeration units avg: 0.0012903225806451613 per sqft Electrical upgrade
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²)
| Office | 0.5 | Office | 0.5 | Office | 0.5 | Office | 0.5
| DryStorage | 0.5 | DryStorage | 0.5 | DryStorage | 0.5 | DryStorage | 0.5
| Deli | 1.5 | Deli | 1.5 | Deli | 1.5 | Deli | 1.5
| Sales | 0.5 | Sales | 0.5 | Sales | 0.5 | Sales | 0.5
| Produce | 0.5 | Produce | 0.5 | Produce | 0.5 | Produce | 0.5
| Bakery | 1.5 | Bakery | 1.5 | Bakery | 1.5 | Bakery | 1.5
Gas Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²) | Post 1950s- DOE reference model Pre-1950s- no data, assume same as post-1950
| Office | 0 | Office | 0 | Office | 0 | Office | 0
| DryStorage | 0 | DryStorage | 0 | DryStorage | 0 | DryStorage | 0
| Deli | 25 | Deli | 25 | Deli | 25 | Deli | 10
| Sales | 0 | Sales | 0 | Sales | 0 | Sales | 0
| Produce | 0 | Produce | 0 | Produce | 0 | Produce | 0
| Bakery | 25 | Bakery | 25 | Bakery | 25 | Bakery | 10
Process Loads | Process Load Type | Equipment Load | Process Load Type | Equipment Load | Process Load Type | Equipment Load | Process Load Type | Equipment Load |  | Process load (Individual Variables) Number of servers avg: 0 per sqft Cooking fuel source Electricity used for cooking 100% Yes Manufacturing fuel source | Cooking fuel source Propane used for cooking 50% Yes Process load (Individual Variables) Number of servers avg: 9.75609756097561e-05 per sqft Manufacturing fuel source | Cooking fuel source Process load (Individual Variables) Number of servers avg: 0 per sqft Manufacturing fuel source | Cooking fuel source Propane used for cooking 67% Yes Electricity used for cooking 67% Yes Natural gas used for cooking 33% Yes Process load (Individual Variables) Number of servers avg: 4.878048780487805e-05 per sqft Manufacturing fuel source
|  | (W) |  | (W) |  | (W) |  | (W)
| N/A |  | N/A |  | N/A |  | N/A
Refrigeration
Cases | Space, Case | Cooling Capacity | Space, Case | Cooling Capacity | Space, Case | Cooling Capacity | Space, Case | Cooling Capacity | Post 1950s- DOE reference model Pre-1950s- no data, assume same as post-1950
|  | (W) |  | (W) |  | (W) |  | (W) | [5 empty] | Should refrigeration be constant across all vintages?
| Bakery, Walk-In Freezer | 276.912 | Bakery, Walk-In Freezer | 1107.648 | Bakery, Walk-In Freezer | 1107.648 | Bakery, Walk-In Freezer | 830.736
| Deli, Dairy and Deli Case | 1081.6875 | Deli, Dairy and Deli Case | 4326.75 | Deli, Dairy and Deli Case | 4326.75 | Deli, Dairy and Deli Case | 3245.0625
| Deli, Walk-In Freezer | 553.824 | Deli, Walk-In Freezer | 2215.296 | Deli, Walk-In Freezer | 2215.296 | Deli, Walk-In Freezer | 1661.472
| Produce, Multideck Case | 10816.875 | Produce, Multideck Case | 43267.5 | Produce, Multideck Case | 43267.5 | Produce, Multideck Case | 32450.625
| Sales, Meat Case | 12107.6887 | Sales, Meat Case | 48430.755 | Sales, Meat Case | 48430.755 | Sales, Meat Display Case | 36323.0662
| Sales, Dairy and Deli Case | 17757.7031 | Sales, Dairy and Deli Case | 71030.8125 | Sales, Dairy and Deli Case | 71030.8125 | Sales, Dairy and Deli Case | 53273.1094
| Sales, Frozen Food | 10996.2909 | Sales, Frozen Food | 43985.1636 | Sales, Frozen Food | 43985.1636 | Sales, Frozen Food | 32988.8727
| Sales, Ice Cream Display | 5157.4146 | Sales, Ice Cream Display | 20629.6583 | Sales, Ice Cream Display | 20629.6583 | Sales, Ice Cream Display | 15472.2437
| Sales, Walk-In Freezer 1 | 1204.5672 | Sales, Walk-In Freezer 1 | 4818.2688 | Sales, Walk-In Freezer 1 | 4818.2688 | Sales, Walk-In Freezer 1 | 3613.7016
| Sales, Walk-In Freezer 2 | 11152.6308 | Sales, Walk-In Freezer 2 | 44610.5232 | Sales, Walk-In Freezer 2 | 44610.5232 | Sales, Walk-In Freezer 2 | 33457.8924
| Sales, Walk-In Freezer 3 | 5861.304 | Sales, Walk-In Freezer 3 | 23445.216 | Sales, Walk-In Freezer 3 | 23445.216 | Sales, Walk-In Freezer 3 | 17583.912
Condenser | Condenser Name | Equipment Load | Condenser Name | Equipment Load | Condenser Name | Equipment Load | Condenser Name | Equipment Load
|  | (W) |  | (W) |  | (W) |  | (W) | Post 1950s- DOE reference model Pre-1950s- no data, assume same as post-1950
| Rack A Condenser | 1125 | Rack A Condenser | 4500 | Rack A Condenser | 4500 | Rack A Condenser | 4500
| Rack B Condenser | 1125 | Rack B Condenser | 4500 | Rack B Condenser | 4500 | Rack B Condenser | 4500
| Rack C Condenser | 1125 | Rack C Condenser | 4500 | Rack C Condenser | 4500 | Rack C Condenser | 4500
| Rack D Condenser | 1125 | Rack D Condenser | 4500 | Rack D Condenser | 4500 | Rack D Condenser | 4500
Schedules
Internal Gain Schedules | Space Type | Schedule | Space Type | Schedule | Space Type | Schedule | Space Type | Schedule | Post 1950s- DOE reference model Pre-1950s- no data, assume same as post-1950
| Office | BLDG_OCC_SCH | Office | BLDG_OCC_SCH | Office | BLDG_OCC_SCH | Office | BLDG_OCC_SCH
| DryStorage | BLDG_OCC_SCH | DryStorage | BLDG_OCC_SCH | DryStorage | BLDG_OCC_SCH | DryStorage | BLDG_OCC_SCH
| Deli | BLDG_OCC_SCH | Deli | BLDG_OCC_SCH | Deli | BLDG_OCC_SCH | Deli | BLDG_OCC_SCH
| Sales | BLDG_OCC_SCH | Sales | BLDG_OCC_SCH | Sales | BLDG_OCC_SCH | Sales | BLDG_OCC_SCH
| Produce | BLDG_OCC_SCH | Produce | BLDG_OCC_SCH | Produce | BLDG_OCC_SCH | Produce | BLDG_OCC_SCH
| Bakery | BLDG_OCC_SCH | Bakery | BLDG_OCC_SCH | Bakery | BLDG_OCC_SCH | Bakery | BLDG_OCC_SCH
| #REF! | Example: Lobby |  |  |  |  | #REF! | Example: Lobby
| #REF! | Example: Kitchen |  |  |  |  | #REF! | Example: Kitchen
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Kitchen |  |  |  |  | #REF! | Example: Kitchen
| #REF! | Example: Lobby |  |  |  |  | #REF! | Example: Lobby
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
Process Load Schedules | Process Load Type | Schedule | Process Load Type | Schedule | Process Load Type | Schedule | Process Load Type | Schedule | Post 1950s- DOE reference model Pre-1950s- no data, assume same as post-1950
| N/A |  | N/A |  | N/A |  | N/A
Building Hours of Operation | Occupied 7 days, 7 am to 10 pm, varying throughout the day |  | Occupied 7 days, 7 am to 10 pm, varying throughout the day |  | Occupied 7 days, 7 am to 10 pm, varying throughout the day |  | Occupied 7 days, 7 am to 10 pm, varying throughout the day
HVAC Airside
Primary HVAC System Type - Dominant space type | Packaged CAV rooftop air conditioning with HW coil |  | Six packaged rooftop air conditioners (one per zone) with electric cooling coil and gas heating coil |  | Six packaged rooftop air conditioners (one per zone) with electric cooling coil and gas heating coil |  | Six packaged rooftop air conditioners (one per zone) with electric cooling coil and gas heating coil |  | Post-1950- DOE reference model Pre-1950s- CBECS | Heating ventilation type Heating ventilation: Central air handling with CAV 50% Yes Cooling ventilation type Cooling ventilation: Central air-handling unit with CAV 100% Yes Main heating equipment 50% Boilers inside (or adjacent to) the building that produce steam or hot water 50% Furnaces that heat air directly, without using steam or hot water HVAC equipment upgrade 50% Yes | Heating ventilation type Heating ventilation: Central air handling with CAV 50% Yes Main heating equipment 50% Individual space heaters (other than heat pumps) 50% Packaged central unit (roof mounted) HVAC equipment upgrade | Heating ventilation type Heating ventilation: Central air handling with CAV 100% Yes Cooling ventilation type Cooling ventilation: Central air-handling unit with CAV 100% Yes Main heating equipment 100% Furnaces that heat air directly, without using steam or hot water HVAC equipment upgrade | Heating ventilation type Heating ventilation: Demand controlled ventilation 33% Yes Heating ventilation: Central air handling with CAV 67% Yes Cooling ventilation type Cooling ventilation: Central air-handling unit with CAV 100% Yes Cooling ventilation: Demand controlled ventilation 33% Yes Main heating equipment 67% Packaged central unit (roof mounted) HVAC equipment upgrade 33% Yes | Should the system types be changed? CBECS suggests central airhandlers.
Other HVAC System Type(s) | Exhaust fans for Bakery, Deli, and Sales zones |  | Exhaust fans for Bakery, Deli, and Sales zones |  | Exhaust fans for Bakery, Deli, and Sales zones |  | Exhaust fans for Bakery, Deli, and Sales zones |  | Post 1950s- DOE reference model Pre-1950s- no data, assume same as post-1950
System Parameters and Controls (Economizer, DCV, energy recovery, etc.) | Programmable thermostat |  | Differential Dry Bulb Economizer for DryStorage, Deli, Sales, Produce, and Bakery |  | Differential Dry Bulb Economizer for DryStorage, Deli, Sales, Produce, and Bakery |  | Differential Dry Bulb Economizer for DryStorage, Deli, Sales, and Produce |  | Post-1950- DOE reference model Pre-1950s- CBECS | How reduce cooling 50% Programmable thermostat Economizer cycle How reduce heating 50% Manually change thermostat 50% Programmable thermostat | How reduce cooling 50% Manually shut down equipment How reduce heating 50% Manually change thermostat 50% Manually shut down equipment | How reduce cooling 100% Manually change thermostat Economizer cycle How reduce heating 100% Manually change thermostat | How reduce cooling 33% Part of the Building Automation System 33% Manually shut down equipment Economizer cycle 67% Yes
HVAC Waterside
Cooling Source Parameters | Packaged DX unit with COP 2.6 |  | Six DX coils, one per packaged air conditioner (one per zone), with COP: Office: 3.50 DryStorage: 3.23 Deli: 3.30 Sales: 3.13 Produce: 3.23 Bakery: 3.30 |  | Six DX coils, one per packaged air conditioner (one per zone), with COP: Office: 3.50 DryStorage: 3.23 Deli: 3.30 Sales: 3.13 Produce: 3.23 Bakery: 3.30 |  | Six DX coils, one per packaged air conditioner (one per zone), with COP: Office: 3.67 DryStorage: 3.23 Deli: 3.30 Sales: 3.13 Produce: 3.23 Bakery: 3.50 |  | Post-1950- DOE reference model Pre-1950s- CBECS, DX cooling, 100% replaced. Assume ASHRAE 90.1-2004 efficiency | Main cooling replaced 100% Yes Cooling fuel source Electricity used for cooling 100% Yes | Main cooling replaced Cooling fuel source Electricity used for cooling 50% Yes | Main cooling replaced Cooling fuel source Electricity used for cooling 100% Yes | Cooling fuel source Electricity used for cooling 100% Yes
Chilled Water Loop & Pump Parameters | N/A |  | N/A |  | N/A |  | N/A
Condenser Water Loop & Pump Parameters | N/A |  | N/A |  | N/A |  | N/A
Cooling tower Parameters | N/A |  | N/A |  | N/A |  | N/A
Heating Source Parameters | Fuel-oil fired hot water boiler, 70% efficiency |  | Six gas heating coils, one per packaged air conditioner (one per zone), with efficiency: Office: 0.78 DryStorage: 0.78 Deli: 0.78 Sales: 0.78 Produce: 0.78 Bakery: 0.78 |  | Six gas heating coils, one per packaged air conditioner (one per zone), with efficiency: Office: 0.80 DryStorage: 0.78 Deli: 0.78 Sales: 0.78 Produce: 0.78 Bakery: 0.78 |  | Six gas heating coils, one per packaged air conditioner (one per zone), with efficiency: Office: 0.80 DryStorage: 0.78 Deli: 0.78 Sales: 0.78 Produce: 0.78 Bakery: 0.80 |  | Post-1950- DOE reference model Pre-1950s- CBECS, fuel oil fired furnace, 100% replaced | Heating fuel source Fuel oil used for main heating 50% Yes Propane used for main heating 50% Yes Main heating replaced 100% Yes | Heating fuel source Fuel oil used for main heating 50% Yes Electricity used for main heating 50% Yes Main heating replaced | Heating fuel source Natural gas used for main heating 100% Yes Main heating replaced | Heating fuel source Fuel oil used for main heating 33% Yes Natural gas used for main heating 33% Yes | 50% boiler, 50% furnace; 50% fuel oil, 50% propane. Which to use?
Hot Water Loop & Pump Parameters | Example: See HVAC Tab |  | N/A |  | N/A |  | N/A
Service Hot Water
Domestic Hot Water System Parameters | Fuel-oil fired DHW boiler, 60% efficient |  | Natural gas fired water heater with 80% efficiency |  | Natural gas fired water heater with 78% efficiency |  | Natural gas fired water heater with 80% efficiency |  | Post-1950- DOE reference model Pre-1950s- CBECS, fuel oil fired boiler | DHW fuel source Electricity used for water heating 50% Yes Propane used for water heating 50% Yes Fuel oil used for water heating 50% Yes Plumbing system upgrade 50% Yes | DHW fuel source Electricity used for water heating 100% Yes Plumbing system upgrade | Plumbing system upgrade DHW fuel source Electricity used for water heating 100% Yes | DHW fuel source Electricity used for water heating 100% Yes Natural gas used for water heating 33% Yes Plumbing system upgrade | 33% propane, fuel oil, electric. Which to use? Electricity seems to be most common (CBECS).
Renewable Energy Systems
Renewable Energy System Description and Parameters | N/A |  | N/A |  | N/A |  | N/A
General Notes
Notes

## Pre-1950 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/person/day) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Office | Y | Occupied 7 days, 7 am to 10 pm | 55 | 60 | 78 | 80 | N/A | N/A | 6.7 | 21.188 | 0 | 0 | 0 | N | N/A | UnitarySingle |  | Unitary | HotWater |  |  | 2.6 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.6
DryStorage | Y | Occupied 7 days, 7 am to 10 pm | 55 | 60 | 78 | 80 | N/A | N/A | 0 | 0 | 0.1477 | 0 | 0 | N | N/A | UnitarySingle |  | Unitary | HotWater |  |  | 2.6 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.6
Deli | Y | Occupied 7 days, 7 am to 10 pm | 55 | 60 | 78 | 80 | N/A | N/A | 6.2 | 0 | 0.29539 | 1.24 | 0 | N | N/A | UnitarySingle |  | Unitary | HotWater |  |  | 2.6 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.6
Sales | Y | Occupied 7 days, 7 am to 10 pm | 55 | 60 | 78 | 80 | N/A | N/A | 0 | 0 | 0.29539 | 0 | 0 | N | N/A | UnitarySingle |  | Unitary | HotWater |  |  | 2.6 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.6
Produce | Y | Occupied 7 days, 7 am to 10 pm | 55 | 60 | 78 | 80 | N/A | N/A | 6.7 | 0 | 0.29539 | 0 | 0 | N | N/A | UnitarySingle |  | Unitary | HotWater |  |  | 2.6 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.6
Bakery | Y | Occupied 7 days, 7 am to 10 pm | 55 | 60 | 78 | 80 | N/A | N/A | 6.7 | 0 | 0.29539 | 0.33 | 0 | N | N/A | UnitarySingle |  | Unitary | HotWater |  |  | 2.6 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.6

## 1950-1980 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/person/day) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Office | Y | Occupied 7 days, 7 am to 10 pm | 55 | 60 | 75.2 | 80 | N/A | N/A | 6.7 | 21.188 | 0 | 0 | 0 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.5 |  |  | 0.8 | NaturalGas | 0.8
DryStorage | Y | Occupied 7 days, 7 am to 10 pm | 55 | 60 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.1477 | 0 | 0 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.23 |  |  | 0.8 | NaturalGas | 0.8
Deli | Y | Occupied 7 days, 7 am to 10 pm | 55 | 60 | 75.2 | 80 | N/A | N/A | 6.2 | 0 | 0.29539 | 1.24 | 0 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.3 |  |  | 0.8 | NaturalGas | 0.8
Sales | Y | Occupied 7 days, 7 am to 10 pm | 55 | 60 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.29539 | 0 | 0 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.13 |  |  | 0.8 | NaturalGas | 0.8
Produce | Y | Occupied 7 days, 7 am to 10 pm | 55 | 60 | 75.2 | 80 | N/A | N/A | 6.7 | 0 | 0.29539 | 0 | 0 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.23 |  |  | 0.8 | NaturalGas | 0.8
Bakery | Y | Occupied 7 days, 7 am to 10 pm | 55 | 60 | 75.2 | 80 | N/A | N/A | 6.7 | 0 | 0.29539 | 0.33 | 0 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.3 |  |  | 0.8 | NaturalGas | 0.8
f

## 1980-2000 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/person/day) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Office | Y | Occupied 7 days, 7 am to 10 pm | 55 | 60 | 75.2 | 80 | N/A | N/A | 6.7 | 21.188 | 0 | 0 | 0 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.5 |  |  | 0.8 | NaturalGas | 0.78
DryStorage | Y | Occupied 7 days, 7 am to 10 pm | 55 | 60 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.1477 | 0 | 0 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.23 |  |  | 0.8 | NaturalGas | 0.78
Deli | Y | Occupied 7 days, 7 am to 10 pm | 55 | 60 | 75.2 | 80 | N/A | N/A | 6.2 | 0 | 0.29539 | 1.24 | 0 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.3 |  |  | 0.8 | NaturalGas | 0.78
Sales | Y | Occupied 7 days, 7 am to 10 pm | 55 | 60 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.29539 | 0 | 0 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.13 |  |  | 0.8 | NaturalGas | 0.78
Produce | Y | Occupied 7 days, 7 am to 10 pm | 55 | 60 | 75.2 | 80 | N/A | N/A | 6.7 | 0 | 0.29539 | 0 | 0 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.23 |  |  | 0.8 | NaturalGas | 0.78
Bakery | Y | Occupied 7 days, 7 am to 10 pm | 55 | 60 | 75.2 | 80 | N/A | N/A | 6.7 | 0 | 0.29539 | 0.33 | 0 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.3 |  |  | 0.8 | NaturalGas | 0.78

## Post-2000 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/person/day) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Office | Y | Occupied 7 days, 7 am to 10 pm | 60 | 63 | 75.2 | 80 | N/A | N/A | 0 | 21.188 | 0 | 0 | 0 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.67 |  |  | 0.8 | NaturalGas | 0.8
DryStorage | Y | Occupied 7 days, 7 am to 10 pm | 60 | 63 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.1477 | 0 | 0 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.23 |  |  | 0.8 | NaturalGas | 0.8
Deli | Y | Occupied 7 days, 7 am to 10 pm | 60 | 63 | 75.2 | 80 | N/A | N/A | 6.2 | 0 | 0.29539 | 1.24 | 0 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.3 |  |  | 0.8 | NaturalGas | 0.8
Sales | Y | Occupied 7 days, 7 am to 10 pm | 60 | 63 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.29539 | 0 | 0 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.13 |  |  | 0.8 | NaturalGas | 0.8
Produce | Y | Occupied 7 days, 7 am to 10 pm | 60 | 63 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.29539 | 0 | 0 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.23 |  |  | 0.8 | NaturalGas | 0.8
Bakery | Y | Occupied 7 days, 7 am to 10 pm | 60 | 63 | 75.2 | 80 | N/A | N/A | 6.7 | 0 | 0.29539 | 0.33 | 0 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.5 |  |  | 0.8 | NaturalGas | 0.8

## Pre-1950 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Office | Office | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Office | Office | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Electric and Gas Loads | Electric and Gas Loads | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15
|  | Sun/Holiday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.15 | 0.15
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - Office | Office | Weekday | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13
|  | Sun/Holiday | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Deli Exhaust Fan On/Off | Deli Exhaust Fan On/Off | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## 1950-1980 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Office | Office | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0 | 0 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Office | Office | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Electric and Gas Loads | Electric and Gas Loads | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15
|  | Sun/Holiday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.15 | 0.15
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - Office | Office | Weekday | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13
|  | Sun/Holiday | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Deli Exhaust Fan On/Off | Deli Exhaust Fan On/Off | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## 1980-2000 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Occupancy | Occupancy | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0 | 0 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Lighting | Lighting | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Plug and Gas Loads | Plug and Gas Loads | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15
|  | Sun/Holiday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.15 | 0.15
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - DHW | DHW | Weekday | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13
|  | Sun/Holiday | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Deli Exhaust On/Off | Deli Exhaust On/Off | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## Post-2000 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Occupancy | Occupancy | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0 | 0 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Lighting | Lighting | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Plug and Gas Loads | Plug and Gas Loads | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15
|  | Sun/Holiday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.15 | 0.15
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - DHW | DHW | Weekday | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13
|  | Sun/Holiday | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Deli Exhaust On/Off | Deli Exhaust On/Off | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## Review
Input | Review |  |  |  | Carbon Free Boston |  | Notes:
Calculation |  |  |  |  | 259104-00 |  | - Create a copy of the Review tab for each model review
Notes | [6 empty] | - The reviewer should review the model itself, and not rely on what is documented in the Calc Plan
[5 empty] | Modeller | Reviewer
Reviewed by:
Date of review:
Review type:
Project Information (section to be filled out by modeller prior to review)
Project phase & modelling protocol: | Example: 100% Design Development, ASHRAE 90.1-2010 proposed and baseline model
Link to archived model file:
Link to zoning diagram:
Link to relevant drawing set:
Link to current results:
Link to energy model report:
Self-review of model is complete (Column G) |  | If "No", please indicate why self-review has not been performed:
Questions for reviewer and/or comments about model
Model Metrics | Proposed | Baseline | Benchmark (if known) | Units
Energy Use Intensity (EUI) |  |  |  | kBtu/ft²/year
Heating Plant Capacity |  |  |  | Btu/ft²
Cooling Plant Capacity |  |  |  | ft²/ton
Total Design Supply Airflow |  |  |  | cfm/ft²
Total Outdoor Airflow |  |  |  | cfm/ft²
Documentation and file storage
Inputs documented in this workbook or elsewhere
Files archived and saved in appropriate location on network
Detailed calculations (in support of input values) are documented and saved
Comments
Weather
Appropriate and correct weather file is used. A copy is saved on the network in the "Weather Data" folder.
Climate zone is correct for project location
Appropriate and correct Design Day data is used (check against Basis of Design report)
Comments
Geometry and Shading
Building compass orientation is correct
Building elevation above sea level is correct
Overhangs and/or other shading devices, or site shading, if modelled, are correctly configured in the software
Comments
Zoning
The number of zones in the model is appropriate for the desired level of analysis. Rooms of a similar type and internal load density with the same exposure may be zoned together.
Zoning is the same between model variants, unless variation is justified by an evaluated measure
Comments
Envelope and Construction
Window to gross wall ratio seems reasonable for the building and matches design drawings
Construction types are correctly assigned to proposed and baseline models
Window U-values, SHGC/G-values, and VLT are whole-assembly values (including framing impacts) and are input as required by the software
Opaque U-values are whole-assembly values and are input as required by the software. Insulation values of steel or wood-framed walls are appropriately de-rated in accordance with ASHRAE Appendix A or other reference standard.
U-values of horizontal constructions and glazing are derated for horizontal convection (U-values should be worse than vertical assemblies)
For natural ventilation models: window opening sizes, opening positions and the ventilation methodology are correct
Model accounts for an appropriate level of thermal mass. (Check that construction layer build-up reasonably matches design, or room mass settings are appropriate for the building construction type.)
Modelled infiltration rates are reasonable and identical between model variants, unless modification is justified for a measure evaluation
Comments
Internal Loads
Interior lighting power densities are reasonable given the building use(s)
Decorative lighting is accounted for in lighting power density values or separately, as appropriate
Daylight control is included where appropriate
Credit is taken for reduced lighting power due to occupancy sensors where appropriate
Receptacle loads and occupant densities are the same for all model variants, unless modification is justified for a measure evaluation
Peak and scheduled equipment loads represent anticipated actual draws from the equipment rather than nameplate values
Electrical room: entire building switchgear capacity is not assigned as an electric load
Comments
Schedules
Schedules are the same for all model variants, unless modification is justified for a measure evaluation
Internal load schedules set the load to 100% on for the cooling design condition and 100% off for the heating design condition
Internal gain schedules vary throughout the day appropriately
Schedules used are reasonable (i.e. taken from a reference standard, and/or informed by conversation with building owner)
Any continuous loads have an appropriate schedule applied (e.g. escalators, process equipment)
Elevator schedule is included, if applicable
Exterior lighting schedule or photocell control is included, if applicable
Comments
Space Conditioning
All conditioned zones are assigned to HVAC systems
Any included unconditioned zones are set to be unconditioned in the model
Thermostat setpoints and driftpoints are correct
Comments
Airside Systems
Airside systems reasonably approximate the designed systems
Supply air temperatures and control strategies (e.g. SAT reset, economizer control) match the proposed design and baseline requirements
System schedules are consistent with design (e.g. fan schedules align with occupancy schedules such that the HVAC systems are enabled during occupied hours)
Ventilation is included per the design intent. Ventilation rates meet applicable codes.
Ventilation design flow rates and schedules are identical between model variants unless modification is justified
Exhaust is properly accounted for within the capabilities of the software tool. Room exhaust is distinguished from system level exhaust.
Schedules set the ventilation flows to 100% for the heating and cooling design conditions
Ventilation is scheduled ON during occupied hours and OFF during unoccupied hours, or otherwise according to the design sequence of operation
Demand controlled ventilation is modelled if applicable
Proposed fan power is correctly modelled per the design brake horsepowers and motor efficiencies. Baseline fan power includes any applicable pressure drop adjustments. Any included return and exhaust fan power is accounted for.
Fan drives are modelled correctly as either variable or constant speed
Pressure drop across heat recovery devices is accounted for (and not double counted)
Comments
Waterside Systems and Plant Equipment
Equipment types and efficiencies match the proposed design and baseline requirements
Part-load curves are based on actual equipment data or reasonably approximate part-load performance
Capacity of heating and cooling plants is reasonable (check SF/capacity)
Pumps and heat rejection fans are modelled correctly as either variable or constant speed
Control of the plant equipment in the model reasonably approximates the design sequence of operations (e.g. boiler and chiller staging, loop temperatures and reset controls)
If packaged equipment is used, efficiencies of equipment are broken out into supply fan, condenser fan, and compressor
Domestic hot water has been included for both models, as appropriate
Comments
Utility Rates
Rates are included. They are the same for all model variants, unless modification is justified
If Peak and Off-Peak rates apply, they are correctly implemented
Utility rates change often. Documentation of the utility rate(s) used for the analysis has been saved with the model files.
Comments
Metrics Checks
Building predicted annual energy costs are reasonable
Building EUI (Energy Use Index, energy use per square foot) is relatively close to benchmarks for your building type. Refer to the BEM Toolkit for sources of benchmarking data.
Annual cooling and heating load profiles make sense
The HVAC systems effectively satisfy the building loads (i.e. any "unmet" load hours are acceptable for the analysis). If high unmet loads occur, investigate and revise the model to resolve any problems
Comments
Energy Results by End Use
Differences in energy used by end use category between model variants can be explained by actual measures
Fan and pump power differences between model variants are roughly proportional to cooling and heating differences
Correct and consistent units are used when reporting the energy results
Energy uses which should be the same between variant models (e.g. plug loads) are indeed the same
Percentage of energy used by various end uses is reasonable given the building use(s)
Comments
Review Close-Out
Do the results of the energy model make sense according to experiential expertise, engineering judgment, and rules of thumb? If not, review the results again after the modeller has addressed the review comments.
Comments
LEED Specific Review Items
LEED Minimum Energy Performance Calculator is complete and highlighted comments on the Performance Outputs tab have been addressed.
Modelled floor area and space types are consistent with information reported in PIf3: Occupant and Usage Data.
Modelled system parameters align with the mechanical schedules provided for PIf4: Schedule and Overview Documents.
Modelled outdoor airflow is consistent with design OA reported in IEQp1 62.1 Calculator and AHU schedules.
Outdoor air is modelled per the design in the proposed, and per Appendix G requirements in the baseline.
Whenever credit is taken for demand control ventilation in the Proposed Case, the outside air ventilation rates for the Baseline Case are modelled using minimum ASHRAE 62.1 rates.
Any exceptional calculations have been documented in the LEED Minimum Energy Performance Calculator and a supplemental detailed narrative has been provided.
Any LEED CIRs related to the project have been clearly referenced in the documentation.
Core & shell projects: Model follows LEED C&S Appendices guidance. All unfinished spaces are included and modelled identically in the baseline and proposed, unless tenant lease agreement requires improvement over baseline requirements.
Utility rates are sourced from the same place (either EIA rates or actual utility rates for the project).
District energy systems are modelled per the guidance in the reference manual (v4) or the Treatment of District and Campus Thermal Energy In LEED (v2009).
Tilted surfaces are correctly modelled as walls or roofs as defined by ASHRAE 90.1 (per 90.1-2010, roofs are horizontal or tilted at an angle of less than 60° from horizontal).
Answer Options
Yes
No
Unclear
N/A
Review Type
Condensed
Detailed
Note on B10: Condensed reviews are recommended for earlier project phases. Detailed reviews are recommended for later project phases and/or review of a beginner energy modeler's work.