## Project
Input | General Information |  |  |  | Carbon Free Boston | Whole Building Energy Modelling Calculation Plan
Calculation |  |  |  |  | 259104-00 | Date of last update: 8/28/2017
Notes | [5 empty] | By: Holly Lattin / Ben Brannon
Project Overview |  |  |  | Source/Comments
Project Name | Carbon Free Boston
Project Number | 259104-00
Project Description | Modeling of the building stock for the city of Boston and testing of carbon reduction policies.
Modelling Scope | Prototype models of 15 buildings with conceptual testing of ECMs
Software, Version | EnergyPlus v8.6
Project Start Date | 2017-12-01
Project Completion Date | 2018-08-01
General Data |  |  |  | Source/Comments
Project Vintage | Four vintages to be tested: Pre-1950, 1950-1980, 1980-2000, and post-2000
Principal Building Type | Hotel
Actual Floor Area (Gross) | 122071
Actual Floor Area (Net) | 122071
Modelled Floor Area (Gross) | 122071
Modelled Floor Area (Net)
Benchmark Site Energy Use Intensity (EUI)
Sustainability Targets | N/A
Codes & Standards |  |  |  | Source/Comments
Applicable Codes & Standards | Varies by vintage.
Energy Code Compliance Path | N/A
Geography |  |  |  | Source/Comments
Project Location | Boston, MA
Weather File | Boston-Logan Airport TMY3
Heating and Cooling Design Conditions | ASHRAE 1%/99%
Site Elevation | 20 ft.
Project Climate Zone(s) | ASHRAE CZ5A
Building Orientation | Varies.
Site Shading | Modeled with no shading.
Model Image
Utility rates |  |  |  | Source/Comments
Electricity Rate/Structure | Varies (Eversource and National Grid)
Natural Gas Rate/Structure | Varies
District Heating Rate/Structure
District Cooling Rate/Structure
Other Utility Rates
Carbon Emission Factors |  |  |  | Source/Comments
Electricity (grid-supplied)
Electricity (grid-displaced)
Natural Gas
Other Carbon Emission Factors
Record of Model Files /Runs
At a minimum, file locations should be documented here for each major project milestone.
| File Name | Description | File Reference Location | Date Created | Created By
1 | Example: Iris 1 | Example: Primary model, backups along the way stored at: | Example: \\global.arup.com\americas\Jobs\S-F\240000\245844-00\4 Internal Project Data\4-04 Calculations\Mech\Energy Modeling\Models | Example: 2/2/2007 | Example: Ben Brannon
2 | Example: Iris 2 | Example: Backup of work progress - Basement Complete | Example: C:\... | Example: 3/6/2008 | Example: Ben Brannon
3 | Example: Iris 3 | Example: Backup of work progress - Bldg A L1 and L2 geometry complete | Example: C:\... | Example: 3/6/2008 | Example: Ben Brannon
4 | Example: Iris 4 | Example: Backup of work progress- Building A Geometry complete | Example: C:\... | Example: 3/9/2008 | Example: Ben Brannon
5 | Example: … | Example: … | Example: … | Example: … | Example: Ben Brannon
6
7
8
9
10
11
12
13
14
15

## Units
Input | Units & Filing Structure |  |  | Carbon Free Boston
Calculation |  |  |  | 259104-00
Notes
Model Units (Auto fills to other tabs) |  | Common Unit Conversions
Opaque Construction U-Value | hr-ft²-F/Btu (R-Value) | Divide | by | To Obtain
Slab-on-Grade U-Value / F-Factor | hr-ft²-F/Btu (R-Value) | Btu/hr-ft²-F | 0.1761 | W/m²-K
Glazing Construction U-Value | Btu/hr-ft²-F (U-Value) | SHGC | 0.87 | SC
Glazing Solar Heat Gain | SHGC | cfm/ft² | 0.19685 | L/s/m²
Infiltration / Air Permeability | (cfm/ft² facade) | ft² | 10.764 | m²
Occupant Density | (ft²/person) | ft | 3.28 | m
Occupant Heat Gain | (Btu/h/person) | Btu/h | 3.412 | W
Lighting & Equipment Heat Gains | (W/ft²) | gal | 0.26417 | liters
Process Loads | (W) | gpm | 15.8504 | L/s
Temperature | (°F) | cfm | 2.1189 | L/s
DHW Demand | (gal/minute) | ft H2O | 2.3067 | psi
Occupant-Based Ventilation | (cfm/person) | ft H2O | 0.33456 | kPa
Area-Based Ventilation | (cfm/ft²) | Pa | 249 | in wg
Air Change Requirement | (ACH) | EER | 3.412 | COP
Area | (ft²) | kW | 3.5169 | tons
Airflow | cfm | Btu/h | 12000 | tons
Water flow | gpm | W | 746 | HP
Heating and Cooling Capacity | kBtu/h | To Obtain | by | Multiply
Refrigeration | (W)
Temperature Conversion
Recommended Filing Structure [Link] |  | T(°C) = [T(°F) - 32] × 5/9
01 Correspondence Specific to Energy Modelling |  | T(°F) = T(°C) × 9/5 + 32
02 Calculation Plan
03 Input Data
01 Weather Data
02 Zoning Diagram
03 Envelope Data
04 Lighting Data
05 Equipment and Other Internal Gains
06 Service Hot Water
07 Airside System Data
08 Waterside System Data
09 Utility Data
10 Special Systems
11 Equipment Submetering
04 Model Files
05 Results
06 Reference Documents
Opaque Construction Units
Btu/hr-ft²-F (U-Value)
hr-ft²-F/Btu (R-Value)
W/m²-K (U-Value)
m²-K/W (R-Value)
Slab-on-grade Units
Btu/hr-ft²-F (U-Value)
hr-ft²-F/Btu (R-Value)
Btu/hr-ft-F
W/m²-K (U-Value)
m²-K/W (R-Value)
W/m-K
Solar Heat Gain Units
SHGC
SC
G-Value
Infiltration / Air Permeability Units
(cfm/ft² facade)
(L/s/m² facade)
(cfm/ft² floor area)
(L/s/m² floor area)
ACH
(m³/h-m²)
Occupant Density Units
(ft²/person)
(people/1000 ft²)
(m²/person)
(people/100 m²)
(# of people)
Occupant Heat Gain Units
(Btu/h/person)
(W/person)
Internal Gain Units
(W/ft²)
(W/m²)
Process Load Units
(Btu/h)
(W)
(W/ft²)
(W/m²)
Temperature Units
(°F)
(°C)
DHW Demand Units
(gal/person/hour)
(gal/person/day)
(gal/minute)
(L/person/hour)
(L/person/day)
Occupant-Based Ventilation Units
(cfm/person)
(L/s/person)
Area-Based Ventilation Units
(cfm/ft²)
(L/s/m²)
(ACH)
Air-Change Requirements
(cfm)
(L/s)
(ACH)
Area
(ft²)
(m²)
Airflow
cfm
L/s
m³/s
Water Flow
gpm
L/min
Heating and Cooling Capacity
kBtu/h
kW

## Input Summary
Input | Input Summary | [7 empty] | Copy columns as needed for each model variant. Columns that have been superseded may be hidden. |  |  |  |  | Copy columns as needed for each model variant. Columns that have been superseded may be hidden. | Carbon Free Boston
Calculation | [14 empty] | 259104-00
Notes
[10 empty] | CBECS -1950, sample size: 1 | CBECS 1950-1980, sample size: 3 | CBECS 1980-2000, sample size: 3 | CBECS 2000-, sample size: 3
| Pre-1950 |  | 1950-1980 |  | 1980-2000 |  | Post-2000 |  | Source / Comments |  |  |  |  | For Further Discussion
Envelope
| Value | Units | Value | Units | Value | Units | Value | Units
Exterior Wall R-Value | [9 empty] | Wall construction material 100% Brick, stone, or stucco Exterior wall replacement Insulation upgrade | Wall construction material 33% Brick, stone, or stucco 67% Concrete block or poured concrete (above grade) Exterior wall replacement 33% Yes Insulation upgrade | Wall construction material 67% Brick, stone, or stucco 33% Aluminum, asbestos, plastic, or wood materials (siding, shingles, tiles, or shakes) Exterior wall replacement Insulation upgrade | Wall construction material 33% Pre-cast concrete panels 33% Aluminum, asbestos, plastic, or wood materials (siding, shingles, tiles, or shakes) 33% Sheet metal panels
Mass Wall - Commercial | 2.4186 | hr-ft²-F/Btu (R-Value) | 6.41 | hr-ft²-F/Btu (R-Value) | 10 | hr-ft²-F/Btu (R-Value) | 8.14 | hr-ft²-F/Btu (R-Value) | Post-1950- DOE reference model Pre-1950s- Assume brick wall (R-2.4) with no insulation. Assume no insulation upgrade.(CBECS) |  |  |  |  | Is the Pre-1950 assumptions realistic? Such low u-values would probably make the hotel rooms uncomfortable. (CBECS sample size small.)
Mass Wall - Residential | 2.4186 | hr-ft²-F/Btu (R-Value) | 6.41 | hr-ft²-F/Btu (R-Value) | 10 | hr-ft²-F/Btu (R-Value) | 11.11 | hr-ft²-F/Btu (R-Value)
Roof R-Value | 2.46 | hr-ft²-F/Btu (R-Value) | 14.2 | hr-ft²-F/Btu (R-Value) | 19.18 | hr-ft²-F/Btu (R-Value) | 16.18 | hr-ft²-F/Btu (R-Value) | Post-1950- DOE reference model Pre-1950s- Assume Wood Framing (R-2.46) with no insulation. Assume no insulation upgrade.(CBECS) | Roof replacement Roof construction material 100% Slate or tile shingles | Roof replacement 33% Yes Roof construction material 100% Built-up (tar, felts, or fiberglass and a ballast, such as stone) | Roof replacement 33% Yes Roof construction material 33% Plastic, rubber, or synthetic sheeting (single or multiple ply) 33% Built-up (tar, felts, or fiberglass and a ballast, such as stone) 33% Metal surfacing | Roof construction material 67% Plastic, rubber, or synthetic sheeting (single or multiple ply) 33% Metal surfacing | Is the Pre-1950 assumptions realistic? Such low u-values would probably make the hotel rooms uncomfortable. (CBECS sample size small.)
Floor: Slab-on-grade R-Value / F-Factor | 3.05 | hr-ft²-F/Btu (R-Value) | 3.05 | hr-ft²-F/Btu (R-Value) | 3.05 | hr-ft²-F/Btu (R-Value) | 3.05 | hr-ft²-F/Btu (R-Value) | Post-1950- DOE reference model Pre-1950s- assume same as post-1950
Underground Walls R-Value | 1.74 | hr-ft²-F/Btu (R-Value) | 1.74 | hr-ft²-F/Btu (R-Value) | 11.73 | hr-ft²-F/Btu (R-Value) | 1.74 | hr-ft²-F/Btu (R-Value) | Post-1950- DOE reference model Pre-1950s- assume same as post-1950
Window to Wall Ratio | 27 | % | 27 | % | 27 | % | 27 | % | Post-1950- DOE reference model Pre-1950s- assume same as post-1950 | Percent exterior glass 100% 2 to 10 percent | Percent exterior glass 33% 11 to 25 percent 33% 51 to 75 percent | Percent exterior glass 33% 11 to 25 percent 67% 2 to 10 percent | Percent exterior glass 33% 11 to 25 percent 33% 2 to 10 percent | CBECS data shows lower WWR. Consider adjusting this.
Glazing Assembly R-Value | [9 empty] | Window replacement Tinted window glass Window glass type 100% Single layer glass | Window replacement 33% Yes Tinted window glass Window glass type 33% Combination of both 67% Multi-layer glass | Window replacement Tinted window glass 67% Yes Window glass type 100% Multi-layer glass | Tinted window glass 67% Yes Window glass type 100% Multi-layer glass
Hotel Room Windows | 1.2 | Btu/hr-ft²-F (U-Value) | 0.62 | Btu/hr-ft²-F (U-Value) | 0.59 | Btu/hr-ft²-F (U-Value) | 0.57 | Btu/hr-ft²-F (U-Value) | Post-1950- DOE reference model Pre-1950s- Assuming historic rolled steel sash with single glazing (U-1.3, according to ASHRAE HANDBOOK 1977 Fundamentals). 100% single pane windows and 0% of the windows have been replaced based on CBECS statistics. |  |  |  |  | Is the pre-1950 glazing performance really that much worse than post-1950?
Lobby/Restaurant/Common Area Windows | 1.2 | Btu/hr-ft²-F (U-Value) | 0.62 | Btu/hr-ft²-F (U-Value) | 0.59 | Btu/hr-ft²-F (U-Value) | 0.57 | Btu/hr-ft²-F (U-Value)
Glazing Assembly Solar Heat Gain
Hotel Room Windows | 0.8 | SHGC | 0.41 | SHGC | 0.39 | SHGC | 0.39 | SHGC | Post-1950- DOE reference model Pre-1950: SHGC 0.8 (http://www.energy.ca.gov/title24/archive/2001standards/residential_manual/res_manual_form_s.PDF ) |  |  |  |  | Is the pre-1950 glazing performance really that much worse than post-1950?
Lobby/Restaurant/Common Area Windows | 0.8 | SHGC | 0.41 | SHGC | 0.39 | SHGC | 0.39 | SHGC
Glazing Assembly VLT
Hotel Room Windows | 70% | % | 32% | % | 31% | % | 31% | % | Post-1950- DOE reference model Pre-1950s- VLT 70% (https://tyvekbku.com/reading/SG_WindowTechnologies_EnergyImpact.pdf)
Lobby/Restaurant/Common Area Windows | 70% | % | 32% | % | 31% | % | 31% | %
Skylight to Roof Ratio | N/A | % | N/A | % | N/A | % | N/A | %
Skylight U-Value | N/A | Btu/hr-ft²-F (U-Value) | N/A | Btu/hr-ft²-F (U-Value) | N/A | Btu/hr-ft²-F (U-Value) | N/A | Btu/hr-ft²-F (U-Value)
Skylight Solar Heat Gain | N/A | SHGC | N/A | SHGC | N/A | SHGC | N/A | SHGC
Skylight VLT | N/A | % | N/A | % | N/A | % | N/A | %
Local Shading Devices | N/A |  | N/A |  | N/A |  | N/A |  |  | External overhangs or awnings | External overhangs or awnings | External overhangs or awnings | External overhangs or awnings 33% Yes
Infiltration / Air Permeability | 2.25 | (cfm/ft² facade) | 1.5 | (cfm/ft² facade) | 1.5 | (cfm/ft² facade) | 0.4 | (cfm/ft² facade) | Post-1950- DOE reference model Pre-1950s- Assume 50% increase compared to 1950-1980.
Occupancy
Occupant Density | Space Type | Occupant Density | Space Type | Occupant Density | Space Type | Occupant Density | Space Type | Occupant Density |  | Occupancy (Individual Variables) Number of employees avg: 0.00016949152542372882 per sqft Number of guest rooms avg: 0.001694915254237288 per sqft | Occupancy (Individual Variables) Number of employees avg: 0.0003392156862745098 per sqft Number of guest rooms avg: 0.001196078431372549 per sqft | Occupancy (Individual Variables) Number of employees avg: 0.0004466876971608833 per sqft Number of guest rooms avg: 0.0013249211356466876 per sqft | Occupancy (Individual Variables) Number of employees avg: 8.152173913043479e-05 per sqft Number of guest rooms avg: 0.0015694219340896814 per sqft
|  | (ft²/person) |  | (ft²/person) |  | (ft²/person) |  | (ft²/person)
| Basement | 400 | Basement | 400 | Basement | 400 | Basement | 400
| Retail | 66.65 | Retail | 66.65 | Retail | 66.65 | Retail | 66.65
| Mech | 0 | Mech | 0 | Mech | 0 | Mech | 0
| Storage | 500 | Storage | 500 | Storage | 500 | Storage | 500
| Laundry | 250 | Laundry | 250 | Laundry | 250 | Laundry | 250
| Cafe | 15 | Cafe | 15 | Cafe | 15 | Cafe | 15
| Lobby | 33.32 | Lobby | 33.32 | Lobby | 33.32 | Lobby | 33.32
| Room | 176 | Room | 176 | Room | 176 | Room | 176
| Corridor | 1000 | Corridor | 1000 | Corridor | 1000 | Corridor | 1000
| Banquet | 15 | Banquet | 15 | Banquet | 15 | Banquet | 15
| Dining | 15 | Dining | 15 | Dining | 15 | Dining | 15
| Kitchen | 200 | Kitchen | 200 | Kitchen | 200 | Kitchen | 200
Lighting & Receptacles
Interior Lighting Power Density | Space Type | Lighting Power Density | Space Type | Lighting Power Density | Space Type | Lighting Power Density | Space Type | Lighting Power Density |  | Lighting type Fluorescent bulbs 100% Yes Compact fluorescent bulbs 100% Yes Lighting upgrade | Lighting type Light-emitting diode (LED) bulbs 33% Yes Incandescent bulbs 100% Yes Fluorescent bulbs 100% Yes High intensity discharge (HID) bulbs 33% Yes Halogen bulbs 33% Yes Compact fluorescent bulbs 100% Yes Lighting upgrade 33% Yes | Lighting type Light-emitting diode (LED) bulbs 67% Yes Incandescent bulbs 67% Yes Fluorescent bulbs 100% Yes High intensity discharge (HID) bulbs 67% Yes Halogen bulbs 33% Yes Compact fluorescent bulbs 100% Yes Lighting upgrade 33% Yes | Lighting type Light-emitting diode (LED) bulbs 67% Yes Fluorescent bulbs 67% Yes Compact fluorescent bulbs 100% Yes | Is post-2000 lighting so much better than pre-2000 vintages?
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²) | Post-1950- DOE reference model Pre-1950s- 100% fluorescent according to CBECS. Assume same as 1950-1980
| Basement | 0.7 | Basement | 0.7 | Basement | 0.7 | Basement | 0.7
| Retail | 2.5 | Retail | 2.5 | Retail | 2.5 | Retail | 1.5
| Mech | 0.8 | Mech | 0.8 | Mech | 0.8 | Mech | 0.8
| Storage | 0.37 | Storage | 0.37 | Storage | 0.37 | Storage | 0.37
| Laundry | 1.14 | Laundry | 1.14 | Laundry | 1.14 | Laundry | 0.6
| Cafe | 1.56 | Cafe | 1.56 | Cafe | 1.56 | Cafe | 1
| Lobby | 1.89 | Lobby | 1.89 | Lobby | 1.89 | Lobby | 1.1
| Room | 1.25 | Room | 1.25 | Room | 1.25 | Room | 0.75
| Corridor | 1.22 | Corridor | 1.22 | Corridor | 1.22 | Corridor | 0.5
| Banquet | 1.56 | Banquet | 1.56 | Banquet | 1.56 | Banquet | 1
| Dining | 1.56 | Dining | 1.56 | Dining | 1.56 | Dining | 1
| Kitchen | 1.56 | Kitchen | 1.56 | Kitchen | 1.56 | Kitchen | 1.2
Daylighting Controls | N/A |  | N/A |  | N/A |  | N/A |  | Post-1950- DOE reference model Pre-1950s- CBECS
Other Lighting Control Credits | N/A |  | N/A |  | N/A |  | N/A |  | Post-1950- DOE reference model Pre-1950s- CBECS | Lighting controls | Lighting controls Multi-level lighting or dimming 33% Yes Occupancy sensors 33% Yes | Lighting controls Multi-level lighting or dimming 33% Yes | Lighting controls BAS controls lighting 33% Yes Occupancy sensors 67% Yes Light scheduling 33% Yes | Add some lighting controls (CBECS)?
External / Site Lighting Power (W) | Exterior Lights | 27826 | Exterior Lights | 27826 | Exterior Lights | 27826 | Exterior Lights | 16753
Receptacle Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Post-1950- DOE reference model Pre-1950s- assume same as post-1950 | Plug loads (Individual Variables) Number of computers avg: 0.001016949152542373 per sqft Number of residential refrigerators avg: 0.00033898305084745765 per sqft Electrical upgrade | Plug loads (Individual Variables) Number of ice makers avg: 2.832244008714597e-05 per sqft Number of closed case refrigeration units avg: 4.651162790697674e-05 per sqft Number of refrigerated vending machines avg: 2.745098039215686e-05 per sqft Number of walk-in units avg: 1.1627906976744185e-05 per sqft Number of residential refrigerators avg: 0.0002745098039215686 per sqft Number of computers avg: 0.0002182952182952183 per sqft Number of compact refrigerators avg: 0.0010490196078431374 per sqft Electrical upgrade | Plug loads (Individual Variables) Number of ice makers avg: 4.4854881266490766e-05 per sqft Number of closed case refrigeration units avg: 0.00014775725593667546 per sqft Number of refrigerated vending machines avg: 5.804416403785489e-05 per sqft Number of residential refrigerators avg: 1.7021276595744682e-05 per sqft Number of computers avg: 0.00022965299684542587 per sqft Number of compact refrigerators avg: 0.0003911671924290221 per sqft Number of walk-in units avg: 3.16622691292876e-05 per sqft Number of open case refrigeration units avg: 1.7021276595744682e-05 per sqft Electrical upgrade | Plug loads (Individual Variables) Number of computers avg: 5.9782608695652175e-05 per sqft Number of refrigerated vending machines avg: 2.5510204081632654e-05 per sqft Plug load control 33% Yes Number of residential refrigerators avg: 0.0003834510595358224 per sqft Number of closed case refrigeration units avg: 1.0204081632653061e-05 per sqft
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²)
| Basement | 0.5 | Basement | 0.5 | Basement | 0.5 | Basement | 0.5
| Retail | 1 | Retail | 1 | Retail | 1 | Retail | 1
| Mech | 0.5 | Mech | 0.5 | Mech | 0.5 | Mech | 0.5
| Storage | 0.25 | Storage | 0.25 | Storage | 0.25 | Storage | 0.25
| Laundry | 5.73 | Laundry | 5.73 | Laundry | 5.73 | Laundry | 5.73
| Cafe | 0.5 | Cafe | 0.5 | Cafe | 0.5 | Cafe | 0.5
| Lobby | 0.75 | Lobby | 0.75 | Lobby | 0.75 | Lobby | 0.75
| Room | 0.75 | Room | 0.75 | Room | 0.75 | Room | 0.75
| Corridor | 0 | Corridor | 0 | Corridor | 0 | Corridor | 0
| Banquet | 0 | Banquet | 0 | Banquet | 0 | Banquet | 0
| Dining | 6.3 | Dining | 6.3 | Dining | 6.3 | Dining | 6.3
| Kitchen | 47.23 | Kitchen | 47.23 | Kitchen | 47.23 | Kitchen | 47.23
Gas Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²) | Post-1950- DOE reference model Pre-1950s- assume same as post-1950
| Basement | 0 | Basement | 0 | Basement | 0 | Basement | 0
| Retail | 0 | Retail | 0 | Retail | 0 | Retail | 0
| Mech | 0 | Mech | 0 | Mech | 0 | Mech | 0
| Storage | 0 | Storage | 0 | Storage | 0 | Storage | 0
| Laundry | 49.82 | Laundry | 49.82 | Laundry | 49.82 | Laundry | 49.82 | [5 empty] | Is gas used for laundry for all vintages?
| Cafe | 0 | Cafe | 0 | Cafe | 0 | Cafe | 0
| Lobby | 0 | Lobby | 0 | Lobby | 0 | Lobby | 0
| Room | 0 | Room | 0 | Room | 0 | Room | 0
| Corridor | 0 | Corridor | 0 | Corridor | 0 | Corridor | 0
| Banquet | 0 | Banquet | 0 | Banquet | 0 | Banquet | 0
| Dining | 0 | Dining | 0 | Dining | 0 | Dining | 0
| Kitchen | 149.95 | Kitchen | 149.95 | Kitchen | 149.95 | Kitchen | 149.95
Process Loads | Process Load Type | Equipment Load | Process Load Type | Equipment Load | Process Load Type | Equipment Load | Process Load Type | Equipment Load |  | Cooking fuel source Natural gas used for cooking 100% Yes Process load (Individual Variables) Number of servers avg: 0 per sqft Manufacturing fuel source | Cooking fuel source Electricity used for cooking 33% Yes Natural gas used for cooking 33% Yes Process load (Individual Variables) Elevators 67% Yes Data center or server farm sqft category 33% 500 square feet or less Number of servers avg: 1.6632016632016632e-05 per sqft Manufacturing fuel source | Process load (Individual Variables) Elevators 67% Yes Number of servers avg: 1.388888888888889e-05 per sqft Cooking fuel source Natural gas used for cooking 67% Yes Manufacturing fuel source | Cooking fuel source Electricity used for cooking 67% Yes Natural gas used for cooking 33% Yes Process load (Individual Variables) Elevators 67% Yes Number of servers avg: 0 per sqft Manufacturing fuel source | Add some process loads for kitchen equipment?
|  | (W) |  | (W) |  | (W) |  | (W) | Post-1950- DOE reference model Pre-1950s- assume same as post-1950
| Elevators | 122222 | Elevators | 122222 | Elevators | 122222 | Elevators | 122222
Refrigeration
Cases | Space, Case | Cooling Capacity | Space, Case | Cooling Capacity | Space, Case | Cooling Capacity | Space, Case | Cooling Capacity
|  | (W) |  | (W) |  | (W) |  | (W) | Post-1950- DOE reference model Pre-1950s- assume same as post-1950
| Kitchen, Walk-In Freezer | 2686.44 | Kitchen, Walk-In Freezer | 2686.44 | Kitchen, Walk-In Freezer | 2686.44 | Kitchen, Walk-In Freezer | 2686.44 | [5 empty] | Are walk-in-freezer efficiencies constant across vintages?
| Kitchen, Display | 2686.44 | Kitchen, Display | 2686.44 | Kitchen, Display | 2686.44 | Kitchen, Display | 2686.44
Condenser | Condenser Name | Equipment Load | Condenser Name | Equipment Load | Condenser Name | Equipment Load | Condenser Name | Equipment Load
|  | (W) |  | (W) |  | (W) |  | (W) | Post-1950- DOE reference model Pre-1950s- assume same as post-1950
| Rack 1 Condenser | 350 | Rack 1 Condenser | 350 | Rack 1 Condenser | 350 | Rack 1 Condenser | 350
| Rack 2 Condenser | 350 | Rack 2 Condenser | 350 | Rack 2 Condenser | 350 | Rack 2 Condenser | 350
Schedules
Internal Gain Schedules | Space Type | Schedule | Space Type | Schedule | Space Type | Schedule | Space Type | Schedule | Post-1950- DOE reference model Pre-1950s- assume same as post-1950
| Basement | Common_Occ_Sch | Basement | Common_Occ_Sch | Basement | Common_Occ_Sch | Basement | Common_Occ_Sch
| Retail | Common_Occ_Sch | Retail | Common_Occ_Sch | Retail | Common_Occ_Sch | Retail | Common_Occ_Sch
| Mech | None | Mech | None | Mech | None | Mech | None
| Storage | Common_Occ_Sch | Storage | Common_Occ_Sch | Storage | Common_Occ_Sch | Storage | Common_Occ_Sch
| Laundry | Common_Occ_Sch | Laundry | Common_Occ_Sch | Laundry | Common_Occ_Sch | Laundry | Common_Occ_Sch
| Cafe | Common_Occ_Sch | Cafe | Common_Occ_Sch | Cafe | Common_Occ_Sch | Cafe | Common_Occ_Sch
| Lobby | Common_Occ_Sch | Lobby | Common_Occ_Sch | Lobby | Common_Occ_Sch | Lobby | Lobby_Occ_Sch
| Room | GuestRoom_Occ_Sch | Room | GuestRoom_Occ_Sch | Room | GuestRoom_Occ_Sch | Room | GuestRoom_Occ_Sch
| Corridor | Common_Occ_Sch | Corridor | Common_Occ_Sch | Corridor | Common_Occ_Sch | Corridor | Common_Occ_Sch
| Banquet | Common_Occ_Sch | Banquet | Common_Occ_Sch | Banquet | Common_Occ_Sch | Banquet | Common_Occ_Sch
| Dining | Common_Occ_Sch | Dining | Common_Occ_Sch | Dining | Common_Occ_Sch | Dining | Common_Occ_Sch
| Kitchen | Common_Occ_Sch | Kitchen | Common_Occ_Sch | Kitchen | Common_Occ_Sch | Kitchen | Common_Occ_Sch
| #REF! | Example: Lobby |  |  |  |  | #REF! | Example: Lobby
| #REF! | Example: Kitchen |  |  |  |  | #REF! | Example: Kitchen
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Kitchen |  |  |  |  | #REF! | Example: Kitchen
| #REF! | Example: Lobby |  |  |  |  | #REF! | Example: Lobby
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
Process Load Schedules | Process Load Type | Schedule | Process Load Type | Schedule | Process Load Type | Schedule | Process Load Type | Schedule | Post-1950- DOE reference model Pre-1950s- assume same as post-1950
| Elevators | BLDG_ELEVATORS | Elevators | BLDG_ELEVATORS | Elevators | BLDG_ELEVATORS | Elevators | BLDG_ELEVATORS
Building Hours of Operation | 24/7, 7 days per week. Varies by space type |  | 24/7, 7 days per week. Varies by space type |  | 24/7, 7 days per week. Varies by space type |  | 24/7, 7 days per week. Varies by space type
HVAC Airside
Primary HVAC System Type - Dominant space type | Constant Air with reheat in common areas, air-cooled chillers for cooling, natural gas boilers for heating |  | Constant Air with reheat in common areas, air-cooled chillers for cooling, natural gas boilers for heating |  | VAV with reheat in common areas, electric chillers for cooling, natural gas boiler for heating |  | VAV with reheat in common areas, electric chillers for cooling, natural gas boiler for heating |  | Post-1950- DOE reference model Pre-1950s- not reported in CBECS. Assume same as 1950-1980 | HVAC equipment upgrade Main heating equipment 100% Boilers inside (or adjacent to) the building that produce steam or hot water | HVAC equipment upgrade 67% Yes Heating ventilation type Heating ventilation: Central air handling with VAV 33% Yes Heating ventilation: Dedicated outside air system 33% Yes Cooling ventilation type Cooling ventilation: Dedicated outside air system 33% Yes Cooling ventilation: Central air-handling unit with VAV 67% Yes Main heating equipment 33% Individual space heaters (other than heat pumps) 67% Boilers inside (or adjacent to) the building that produce steam or hot water | HVAC equipment upgrade 33% Yes Heating ventilation type Heating ventilation: None of these 33% Yes Heating ventilation: Central air handling with VAV 67% Yes Cooling ventilation type Cooling ventilation: Central air-handling unit with VAV 67% Yes Main heating equipment 33% Boilers inside (or adjacent to) the building that produce steam or hot water 67% Packaged central unit (roof mounted) | Heating ventilation type Heating ventilation: Central air handling with CAV 33% Yes Cooling ventilation type Cooling ventilation: Central air-handling unit with CAV 33% Yes Cooling ventilation: Central air-handling unit with VAV 33% Yes Main heating equipment 67% District steam or hot water piped in from outside the building 33% Heat pumps (other than components of a packaged unit)
Other HVAC System Type(s) | Guest rooms served by 100% OA with four-pipe fan coil |  | Guest rooms served by 100% OA with four-pipe fan coil |  | Guest rooms served by 100% OA with four-pipe fan coil |  | Guest rooms served by 100% OA with four-pipe fan coil |  | Post-1950- DOE reference model Pre-1950s- not reported in CBECS. Assume same as 1950-1980
System Parameters and Controls (Economizer, DCV, energy recovery, etc.) | Differential dry bulb economizer on CAV with reheat |  | Differential dry bulb economizer on CAV with reheat |  | Differential dry bulb economizer on VAV with reheat |  | Differential dry bulb economizer on VAV with reheat |  | Post-1950- DOE reference model Pre-1950s- not reported in CBECS. Assume same as 1950-1980 | How reduce heating 100% Part of the Building Automation System | How reduce cooling 33% Part of the Building Automation System 33% Manually change thermostat Economizer cycle 33% Yes How reduce heating 33% Part of the Building Automation System 33% Manually change thermostat | How reduce cooling 33% Part of the Building Automation System 33% Manually change thermostat Economizer cycle 67% Yes How reduce heating 33% Manually change thermostat 33% Part of the Building Automation System 33% Programmable thermostat | How reduce cooling 33% Part of the Building Automation System Economizer cycle 67% Yes How reduce heating 33% Part of the Building Automation System
HVAC Waterside
Cooling Source Parameters | (2) Electric Air-Cooled Chiler, COP=2.64 |  | (2) Electric Air-Cooled Chiler, COP=2.64 |  | (2) Electric Air-Cooled Chiller, COP = 2.5 |  | (2) Electric Air-Cooled Chiller, COP = 5.5 |  | Post-1950- DOE reference model Pre-1950s- not reported in CBECS. Assume same as 1950-1980 | Cooling fuel source | Main cooling replaced 67% Yes Chiller type Chiller type: Water cooled 33% Yes Cooling fuel source Electricity used for cooling 100% Yes | Main cooling replaced 67% Yes Cooling fuel source Electricity used for cooling 67% Yes | Cooling fuel source District chilled water used for cooling 33% Yes Electricity used for cooling 67% Yes
Chilled Water Loop & Pump Parameters | Variable speed pump, 44F chilled water loop |  | Variable speed pump, 44F chilled water loop |  | Variable speed pump, 44F chilled water loop |  | Variable speed pump, 44F chilled water loop |  | Post-1950- DOE reference model Pre-1950s- not reported in CBECS. Assume same as 1950-1980
Condenser Water Loop & Pump Parameters | N/A |  | N/A |  | N/A |  | N/A |  | Post-1950- DOE reference model Pre-1950s- not reported in CBECS. Assume same as 1950-1980
Cooling tower Parameters | N/A |  | N/A |  | N/A |  | N/A |  | Post-1950- DOE reference model Pre-1950s- not reported in CBECS. Assume same as 1950-1980
Heating Source Parameters | Natural gas boiler, 70% efficient |  | Natural gas boiler, 76% efficient; Unit heater (electric) 100% efficient for top floor corridor |  | Natural gas boiler, 70% efficient; Unit heater (electric) 100% efficient for top floor corridor |  | Natural gas boiler, 78% efficient; Unit heater (electric) 100% efficient for top floor corridor |  | Post-1950- DOE reference model Pre-1950s- natural gas fired boiler from CBECS | Heating fuel source Natural gas used for main heating 100% Yes Main heating replaced 100% Yes | Heating fuel source Natural gas used for main heating 67% Yes Electricity used for main heating 33% Yes Main heating replaced 33% Yes | Heating fuel source Fuel oil used for main heating 33% Yes Electricity used for main heating 67% Yes Main heating replaced 67% Yes | Heating fuel source District steam used for main heating 33% Yes District hot water used for main heating 33% Yes Electricity used for main heating 33% Yes | Add "Unit heater (electric) 100% efficient for top floor corridor" to Pre-1950 (for consistency)?
Hot Water Loop & Pump Parameters | Variable speed pump, 180F heating hot water |  | Variable speed pump, 180F heating hot water |  | Variable speed pump, 180F heating hot water |  | Variable speed pump, 180F heating hot water |  | Post-1950- DOE reference model Pre-1950s- not reported in CBECS. Assume same as 1950-1980
Service Hot Water
Domestic Hot Water System Parameters | Natural gas fired instantaneous water heater, 80% efficient. |  | Natural gas boiler, 80% efficient, 140F loop temperature, variable speed pump |  | Natural gas boiler, 78% efficient, 140F loop temperature, variable speed pump |  | Natural gas boiler, 80% efficient, 140F loop temperature, variable speed pump |  | Post-1950- DOE reference model Pre-1950s- natural gas fired instantaneous water heater from CBECS | DHW fuel source Natural gas used for water heating 100% Yes Plumbing system upgrade DHW heater type | DHW fuel source Propane used for water heating 33% Yes Natural gas used for water heating 67% Yes Plumbing system upgrade DHW heater type Instant hot water 67% Yes | Plumbing system upgrade DHW fuel source Fuel oil used for water heating 33% Yes Natural gas used for water heating 67% Yes DHW heater type Instant hot water 67% Yes | DHW fuel source District hot water used for water heating 33% Yes Natural gas used for water heating 33% Yes Electricity used for water heating 33% Yes District steam used for water heating 33% Yes Solar used for water heating 33% Yes DHW heater type Instant hot water 100% Yes | Mix of fuels. Change to instantaneuos water heaters (CBECS)? Why is 1980-2000 efficiency worse than 1950-1980? More systems have been replaced?
Renewable Energy Systems
Renewable Energy System Description and Parameters | N/A |  | N/A |  | N/A |  | N/A
General Notes
Notes

## Pre-1950 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/minute) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Basement | Y | Setpoint active 8 am to 12 am | 60.8 | 60.8 | 75.2 | 86 | N/A | N/A | 0 | 0 | 0.05 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.76 | CAV system, but only VAV allows for CHW cooling
Retail | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 0 | 0.3 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.76 | CAV system, but only VAV allows for CHW cooling
Mech | Y | Constant heating or cooling temp | 60.8 | 60.8 | 86 | 86 | N/A | N/A | 0 | 0 | 0.05 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.76 | CAV system, but only VAV allows for CHW cooling
Storage | Y | Constant heating or cooling temp | 60.8 | 60.8 | 86 | 86 | N/A | N/A | 0 | 0 | 0.15 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.76 | CAV system, but only VAV allows for CHW cooling
Laundry | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 2.61 | 16.95 | 0 | 0.6 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.76 | CAV system, but only VAV allows for CHW cooling
Cafe | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 21.19 | 0 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.76 | CAV system, but only VAV allows for CHW cooling
Lobby | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 21.19 | 0 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.76 | CAV system, but only VAV allows for CHW cooling
Room | Y | Constant heating or cooling temp | 63 | 67 | 75.2 | 75.2 | N/A | N/A | 0.0208 | 20 | 0 | 0 | N/A | N | N/A | DedicatedOutdoorAir |  | FanCoil | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.76
Corridor | Y | Constant heating or cooling temp | 60.8 | 60.8 | 86 | 86 | N/A | N/A | 0 | 0 | 0.05 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.76 | CAV system, but only VAV allows for CHW cooling
Banquet | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 21.19 | 0 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.76 | CAV system, but only VAV allows for CHW cooling
Dining | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 21.19 | 0 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.76 | CAV system, but only VAV allows for CHW cooling
Kitchen | Y | Setpoint active 8 am to 12 am | 60.8 | 66.2 | 78.8 | 86 | N/A | N/A | 2.22 | 16.95 | 0 | 3.6 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.76 | CAV system, but only VAV allows for CHW cooling

## 1950-1980 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/minute) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Basement | Y | Setpoint active 8 am to 12 am | 60.8 | 60.8 | 75.2 | 86 | N/A | N/A | 0 | 0 | 0.05 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78 | CAV system, but only VAV allows for CHW cooling
Retail | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 0 | 0.3 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78 | CAV system, but only VAV allows for CHW cooling
Mech | Y | Constant heating or cooling temp | 60.8 | 60.8 | 86 | 86 | N/A | N/A | 0 | 0 | 0.05 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78 | CAV system, but only VAV allows for CHW cooling
Storage | Y | Constant heating or cooling temp | 60.8 | 60.8 | 86 | 86 | N/A | N/A | 0 | 0 | 0.15 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78 | CAV system, but only VAV allows for CHW cooling
Laundry | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 2.61 | 16.95 | 0 | 0.6 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78 | CAV system, but only VAV allows for CHW cooling
Cafe | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 21.19 | 0 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78 | CAV system, but only VAV allows for CHW cooling
Lobby | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 21.19 | 0 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78 | CAV system, but only VAV allows for CHW cooling
Room | Y | Constant heating or cooling temp | 63 | 67 | 75.2 | 75.2 | N/A | N/A | 0.0208 | 20 | 0 | 0 | N/A | N | N/A | DedicatedOutdoorAir |  | FanCoil | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78
Corridor | Y | Constant heating or cooling temp | 60.8 | 60.8 | 86 | 86 | N/A | N/A | 0 | 0 | 0.05 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | Electric | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78 | CAV system, but only VAV allows for CHW cooling
Banquet | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 21.19 | 0 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78 | CAV system, but only VAV allows for CHW cooling
Dining | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 21.19 | 0 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78 | CAV system, but only VAV allows for CHW cooling
Kitchen | Y | Setpoint active 8 am to 12 am | 60.8 | 66.2 | 78.8 | 86 | N/A | N/A | 2.22 | 16.95 | 0 | 3.6 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.64 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78 | CAV system, but only VAV allows for CHW cooling

## 1980-2000 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/minute) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Basement | Y | Setpoint active 8 am to 12 am | 60.8 | 60.8 | 75.2 | 86 | N/A | N/A | 0 | 0 | 0.05 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.5 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78
Retail | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 0 | 0.3 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.5 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78
Mech | Y | Constant heating or cooling temp | 60.8 | 60.8 | 86 | 86 | N/A | N/A | 0 | 0 | 0.05 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.5 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78
Storage | Y | Constant heating or cooling temp | 60.8 | 60.8 | 86 | 86 | N/A | N/A | 0 | 0 | 0.15 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.5 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78
Laundry | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 2.61 | 0 | 0 | 0.6 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.5 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78
Cafe | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 21.19 | 0 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.5 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78
Lobby | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 21.19 | 0 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.5 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78
Room | Y | Constant heating or cooling temp | 63 | 67 | 75.2 | 75.2 | N/A | N/A | 0.0208 | 20 | 0 | 0 | N/A | N | N/A | DedicatedOutdoorAir |  | FanCoil | HotWater | AirCooled | ElectricCentrifugalChiller | 2.5 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78
Corridor | Y | Constant heating or cooling temp | 60.8 | 60.8 | 86 | 86 | N/A | N/A | 0 | 0 | 0.05 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | Electric | AirCooled | ElectricCentrifugalChiller | 2.5 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78
Banquet | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 21.19 | 0 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.5 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78
Dining | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 21.19 | 0 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.5 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78
Kitchen | Y | Setpoint active 8 am to 12 am | 60.8 | 66.2 | 78.8 | 86 | N/A | N/A | 2.22 | 0 | 0 | 3.6 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 2.5 | NaturalGas | HotWaterBoiler | 0.76 | NaturalGas | 0.78

## Post-2000 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/minute) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Basement | Y | Setpoint active 8 am to 12 am | 60.8 | 60.8 | 75.2 | 86 | N/A | N/A | 0 | 0 | 0.05 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8
Retail | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 0 | 0.3 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8
Mech | Y | Constant heating or cooling temp | 60.8 | 60.8 | 86 | 86 | N/A | N/A | 0 | 0 | 0.05 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8
Storage | Y | Constant heating or cooling temp | 60.8 | 60.8 | 86 | 86 | N/A | N/A | 0 | 0 | 0.15 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8
Laundry | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 2.61 | 0 | 0 | 0.6 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8
Cafe | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 21.19 | 0 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8
Lobby | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 21.19 | 0 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8
Room | Y | Constant heating or cooling temp | 63 | 67 | 75.2 | 75.2 | N/A | N/A | 0.0208 | 20 | 0 | 0 | N/A | N | N/A | DedicatedOutdoorAir |  | FanCoil | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8
Corridor | Y | Constant heating or cooling temp | 60.8 | 60.8 | 86 | 86 | N/A | N/A | 0 | 0 | 0.05 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | Electric | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8
Banquet | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 21.19 | 0 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8
Dining | Y | Setpoint active 8 am to 12 am | 60.8 | 68 | 75.2 | 86 | N/A | N/A | 0 | 21.19 | 0 | 0 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8
Kitchen | Y | Setpoint active 8 am to 12 am | 60.8 | 66.2 | 78.8 | 86 | N/A | N/A | 2.22 | 0 | 0 | 3.6 | N/A | N | N/A | Unitary | HotWater | Unitary | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8

## Pre-1950 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Common Areas | Common Areas | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7
|  | Sun/Holiday | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8
Occupancy - Guest Rooms | Guest Rooms | Weekday | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5
|  | Sun/Holiday | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Common Areas | Common Areas | Weekday | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
|  | Sun/Holiday | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
Lighting - Guest Rooms | Guest Rooms | Weekday | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
|  | Sun/Holiday | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Common Areas | Common Areas | Weekday | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4
Receptacles - Guest Rooms | Guest Rooms | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
|  | Sun/Holiday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
Receptacles - Ktichen Electric Equipment | Ktichen Electric Equipment | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Receptacles - Kitchen Gas Equipment | Kitchen Gas Equipment | Weekday | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
|  | Sun/Holiday | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
Receptacles - Laundry Electric Equipment | Laundry Electric Equipment | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Receptacles - Laundry Gas Equipment | Laundry Gas Equipment | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - Kitchen | Kitchen | Weekday | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
|  | Sun/Holiday | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Domestic Hot Water - Guest Room | Guest Room | Weekday | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25
|  | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
|  | Sun/Holiday | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
Domestic Hot Water - Laundry | Laundry | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Elevators | Elevators | Weekday | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4
Process Loads - Kitchen Exhaust Fan | Kitchen Exhaust Fan | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## 1950-1980 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Common Areas | Common Areas | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7
|  | Sun/Holiday | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8
Occupancy - Guest Rooms | Guest Rooms | Weekday | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5
|  | Sun/Holiday | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Common Areas | Common Areas | Weekday | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
|  | Sun/Holiday | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
Lighting - Guest Rooms | Guest Rooms | Weekday | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
|  | Sun/Holiday | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Common Areas | Common Areas | Weekday | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4
Receptacles - Guest Rooms | Guest Rooms | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
|  | Sun/Holiday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
Receptacles - Ktichen Electric Equipment | Ktichen Electric Equipment | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Receptacles - Kitchen Gas Equipment | Kitchen Gas Equipment | Weekday | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
|  | Sun/Holiday | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
Receptacles - Laundry Electric Equipment | Laundry Electric Equipment | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Receptacles - Laundry Gas Equipment | Laundry Gas Equipment | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - Kitchen | Kitchen | Weekday | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
|  | Sun/Holiday | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Domestic Hot Water - Guest Room | Guest Room | Weekday | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25
|  | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
|  | Sun/Holiday | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
Domestic Hot Water - Laundry | Laundry | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Elevators | Elevators | Weekday | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4
Process Loads - Kitchen Exhaust Fan | Kitchen Exhaust Fan | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## 1980-2000 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Common Areas | Common Areas | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7
|  | Sun/Holiday | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8
Occupancy - Guest Rooms | Guest Rooms | Weekday | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5
|  | Sun/Holiday | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Common Areas | Common Areas | Weekday | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
|  | Sun/Holiday | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
Lighting - Guest Rooms | Guest Rooms | Weekday | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33
|  | Sat | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
|  | Sun/Holiday | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Common Areas | Common Areas | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15
|  | Sun/Holiday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.15 | 0.15
Receptacles - Guest Rooms | Guest Rooms | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
|  | Sun/Holiday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
Receptacles - Kitchen Electric Equipment | Kitchen Electric Equipment | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Receptacles - Kitchen Gas Equipment | Kitchen Gas Equipment | Weekday | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
|  | Sun/Holiday | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
Receptacles - Laundry Electric Equipment | Laundry Electric Equipment | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Receptacles - Laundry Gas Equipment | Laundry Gas Equipment | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - Kitchen | Kitchen | Weekday | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
|  | Sun/Holiday | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Domestic Hot Water - Guest Room | Guest Room | Weekday | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25
|  | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
|  | Sun/Holiday | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
Domestic Hot Water - Laundry | Laundry | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Elevators | Elevators | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | DOE Post-1980 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
Process Loads - Kitchen Exhaust | Kitchen Exhaust | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## Post-2000 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Common Spaces | Common Spaces | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7
|  | Sun/Holiday | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8
Occupancy - Guest Rooms | Guest Rooms | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
|  | Sun/Holiday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
Occupancy - Lobby | Lobby | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Common Spaces | Common Spaces | Weekday | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
|  | Sun/Holiday | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
Lighting - Guest Rooms | Guest Rooms | Weekday | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33
|  | Sat | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
|  | Sun/Holiday | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Common Areas | Common Areas | Weekday | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4
|  | Sun/Holiday | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4
Receptacles - Guest Rooms | Guest Rooms | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
|  | Sun/Holiday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
Receptacles - Kitchen Electric Equipment | Kitchen Electric Equipment | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Receptacles - Kitchen Gas Equipment | Kitchen Gas Equipment | Weekday | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
|  | Sun/Holiday | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
Receptacles - Laundry Electric Equipment | Laundry Electric Equipment | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Receptacles - Laundry Gas Equipment | Laundry Gas Equipment | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - Kitchen | Kitchen | Weekday | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
|  | Sun/Holiday | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Domestic Hot Water - Guest Room | Guest Room | Weekday | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
|  | Sun/Holiday | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
Domestic Hot Water - Laundry | Laundry | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Elevators | Elevators | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | DOE 2004 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
Process Loads - Kitchen Exhaust Fan | Kitchen Exhaust Fan | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## Review
Input | Review |  |  |  | Carbon Free Boston |  | Notes:
Calculation |  |  |  |  | 259104-00 |  | - Create a copy of the Review tab for each model review
Notes | [6 empty] | - The reviewer should review the model itself, and not rely on what is documented in the Calc Plan
[5 empty] | Modeller | Reviewer
Reviewed by:
Date of review:
Review type:
Project Information (section to be filled out by modeller prior to review)
Project phase & modelling protocol: | Example: 100% Design Development, ASHRAE 90.1-2010 proposed and baseline model
Link to archived model file:
Link to zoning diagram:
Link to relevant drawing set:
Link to current results:
Link to energy model report:
Self-review of model is complete (Column G) |  | If "No", please indicate why self-review has not been performed:
Questions for reviewer and/or comments about model
Model Metrics | Proposed | Baseline | Benchmark (if known) | Units
Energy Use Intensity (EUI) |  |  |  | kBtu/ft²/year
Heating Plant Capacity |  |  |  | Btu/ft²
Cooling Plant Capacity |  |  |  | ft²/ton
Total Design Supply Airflow |  |  |  | cfm/ft²
Total Outdoor Airflow |  |  |  | cfm/ft²
Documentation and file storage
Inputs documented in this workbook or elsewhere
Files archived and saved in appropriate location on network
Detailed calculations (in support of input values) are documented and saved
Comments
Weather
Appropriate and correct weather file is used. A copy is saved on the network in the "Weather Data" folder.
Climate zone is correct for project location
Appropriate and correct Design Day data is used (check against Basis of Design report)
Comments
Geometry and Shading
Building compass orientation is correct
Building elevation above sea level is correct
Overhangs and/or other shading devices, or site shading, if modelled, are correctly configured in the software
Comments
Zoning
The number of zones in the model is appropriate for the desired level of analysis. Rooms of a similar type and internal load density with the same exposure may be zoned together.
Zoning is the same between model variants, unless variation is justified by an evaluated measure
Comments
Envelope and Construction
Window to gross wall ratio seems reasonable for the building and matches design drawings
Construction types are correctly assigned to proposed and baseline models
Window U-values, SHGC/G-values, and VLT are whole-assembly values (including framing impacts) and are input as required by the software
Opaque U-values are whole-assembly values and are input as required by the software. Insulation values of steel or wood-framed walls are appropriately de-rated in accordance with ASHRAE Appendix A or other reference standard.
U-values of horizontal constructions and glazing are derated for horizontal convection (U-values should be worse than vertical assemblies)
For natural ventilation models: window opening sizes, opening positions and the ventilation methodology are correct
Model accounts for an appropriate level of thermal mass. (Check that construction layer build-up reasonably matches design, or room mass settings are appropriate for the building construction type.)
Modelled infiltration rates are reasonable and identical between model variants, unless modification is justified for a measure evaluation
Comments
Internal Loads
Interior lighting power densities are reasonable given the building use(s)
Decorative lighting is accounted for in lighting power density values or separately, as appropriate
Daylight control is included where appropriate
Credit is taken for reduced lighting power due to occupancy sensors where appropriate
Receptacle loads and occupant densities are the same for all model variants, unless modification is justified for a measure evaluation
Peak and scheduled equipment loads represent anticipated actual draws from the equipment rather than nameplate values
Electrical room: entire building switchgear capacity is not assigned as an electric load
Comments
Schedules
Schedules are the same for all model variants, unless modification is justified for a measure evaluation
Internal load schedules set the load to 100% on for the cooling design condition and 100% off for the heating design condition
Internal gain schedules vary throughout the day appropriately
Schedules used are reasonable (i.e. taken from a reference standard, and/or informed by conversation with building owner)
Any continuous loads have an appropriate schedule applied (e.g. escalators, process equipment)
Elevator schedule is included, if applicable
Exterior lighting schedule or photocell control is included, if applicable
Comments
Space Conditioning
All conditioned zones are assigned to HVAC systems
Any included unconditioned zones are set to be unconditioned in the model
Thermostat setpoints and driftpoints are correct
Comments
Airside Systems
Airside systems reasonably approximate the designed systems
Supply air temperatures and control strategies (e.g. SAT reset, economizer control) match the proposed design and baseline requirements
System schedules are consistent with design (e.g. fan schedules align with occupancy schedules such that the HVAC systems are enabled during occupied hours)
Ventilation is included per the design intent. Ventilation rates meet applicable codes.
Ventilation design flow rates and schedules are identical between model variants unless modification is justified
Exhaust is properly accounted for within the capabilities of the software tool. Room exhaust is distinguished from system level exhaust.
Schedules set the ventilation flows to 100% for the heating and cooling design conditions
Ventilation is scheduled ON during occupied hours and OFF during unoccupied hours, or otherwise according to the design sequence of operation
Demand controlled ventilation is modelled if applicable
Proposed fan power is correctly modelled per the design brake horsepowers and motor efficiencies. Baseline fan power includes any applicable pressure drop adjustments. Any included return and exhaust fan power is accounted for.
Fan drives are modelled correctly as either variable or constant speed
Pressure drop across heat recovery devices is accounted for (and not double counted)
Comments
Waterside Systems and Plant Equipment
Equipment types and efficiencies match the proposed design and baseline requirements
Part-load curves are based on actual equipment data or reasonably approximate part-load performance
Capacity of heating and cooling plants is reasonable (check SF/capacity)
Pumps and heat rejection fans are modelled correctly as either variable or constant speed
Control of the plant equipment in the model reasonably approximates the design sequence of operations (e.g. boiler and chiller staging, loop temperatures and reset controls)
If packaged equipment is used, efficiencies of equipment are broken out into supply fan, condenser fan, and compressor
Domestic hot water has been included for both models, as appropriate
Comments
Utility Rates
Rates are included. They are the same for all model variants, unless modification is justified
If Peak and Off-Peak rates apply, they are correctly implemented
Utility rates change often. Documentation of the utility rate(s) used for the analysis has been saved with the model files.
Comments
Metrics Checks
Building predicted annual energy costs are reasonable
Building EUI (Energy Use Index, energy use per square foot) is relatively close to benchmarks for your building type. Refer to the BEM Toolkit for sources of benchmarking data.
Annual cooling and heating load profiles make sense
The HVAC systems effectively satisfy the building loads (i.e. any "unmet" load hours are acceptable for the analysis). If high unmet loads occur, investigate and revise the model to resolve any problems
Comments
Energy Results by End Use
Differences in energy used by end use category between model variants can be explained by actual measures
Fan and pump power differences between model variants are roughly proportional to cooling and heating differences
Correct and consistent units are used when reporting the energy results
Energy uses which should be the same between variant models (e.g. plug loads) are indeed the same
Percentage of energy used by various end uses is reasonable given the building use(s)
Comments
Review Close-Out
Do the results of the energy model make sense according to experiential expertise, engineering judgment, and rules of thumb? If not, review the results again after the modeller has addressed the review comments.
Comments
LEED Specific Review Items
LEED Minimum Energy Performance Calculator is complete and highlighted comments on the Performance Outputs tab have been addressed.
Modelled floor area and space types are consistent with information reported in PIf3: Occupant and Usage Data.
Modelled system parameters align with the mechanical schedules provided for PIf4: Schedule and Overview Documents.
Modelled outdoor airflow is consistent with design OA reported in IEQp1 62.1 Calculator and AHU schedules.
Outdoor air is modelled per the design in the proposed, and per Appendix G requirements in the baseline.
Whenever credit is taken for demand control ventilation in the Proposed Case, the outside air ventilation rates for the Baseline Case are modelled using minimum ASHRAE 62.1 rates.
Any exceptional calculations have been documented in the LEED Minimum Energy Performance Calculator and a supplemental detailed narrative has been provided.
Any LEED CIRs related to the project have been clearly referenced in the documentation.
Core & shell projects: Model follows LEED C&S Appendices guidance. All unfinished spaces are included and modelled identically in the baseline and proposed, unless tenant lease agreement requires improvement over baseline requirements.
Utility rates are sourced from the same place (either EIA rates or actual utility rates for the project).
District energy systems are modelled per the guidance in the reference manual (v4) or the Treatment of District and Campus Thermal Energy In LEED (v2009).
Tilted surfaces are correctly modelled as walls or roofs as defined by ASHRAE 90.1 (per 90.1-2010, roofs are horizontal or tilted at an angle of less than 60° from horizontal).
Answer Options
Yes
No
Unclear
N/A
Review Type
Condensed
Detailed
Note on B10: Condensed reviews are recommended for earlier project phases. Detailed reviews are recommended for later project phases and/or review of a beginner energy modeler's work.