## Project
Input | General Information |  |  |  | Carbon Free Boston | Whole Building Energy Modelling Calculation Plan
Calculation |  |  |  |  | 259104-00 | Date of last update: 8/28/2017
Notes | [5 empty] | By: Holly Lattin / Ben Brannon
Project Overview |  |  |  | Source/Comments
Project Name | Carbon Free Boston
Project Number | 259104-00
Project Description | Modeling of the building stock for the city of Boston and testing of carbon reduction policies.
Modelling Scope | Prototype models of 15 buildings with conceptual testing of ECMs
Software, Version | EnergyPlus v8.6
Project Start Date | 2017-12-01
Project Completion Date | 2018-08-01
General Data |  |  |  | Source/Comments
Project Vintage | Four vintages to be tested: Pre-1950, 1950-1980, 1980-2000, and post-2000
Principal Building Type | Retail
Actual Floor Area (Gross) | 24684
Actual Floor Area (Net) | 24684
Modelled Floor Area (Gross) | 24684
Modelled Floor Area (Net) | 24684
Benchmark Site Energy Use Intensity (EUI)
Sustainability Targets | N/A
Codes & Standards |  |  |  | Source/Comments
Applicable Codes & Standards | Varies by vintage.
Energy Code Compliance Path | N/A
Geography |  |  |  | Source/Comments
Project Location | Boston, MA
Weather File | Boston-Logan Airport TMY3
Heating and Cooling Design Conditions | ASHRAE 1%/99%
Site Elevation | 20 ft.
Project Climate Zone(s) | ASHRAE CZ5A
Building Orientation | Varies.
Site Shading | Modeled with no shading.
Model Image
Utility rates |  |  |  | Source/Comments
Electricity Rate/Structure | Varies (Eversource and National Grid)
Natural Gas Rate/Structure | Varies
District Heating Rate/Structure
District Cooling Rate/Structure
Other Utility Rates
Carbon Emission Factors |  |  |  | Source/Comments
Electricity (grid-supplied)
Electricity (grid-displaced)
Natural Gas
Other Carbon Emission Factors
Record of Model Files /Runs
At a minimum, file locations should be documented here for each major project milestone.
| File Name | Description | File Reference Location | Date Created | Created By
1 | Example: Iris 1 | Example: Primary model, backups along the way stored at: | Example: \\global.arup.com\americas\Jobs\S-F\240000\245844-00\4 Internal Project Data\4-04 Calculations\Mech\Energy Modeling\Models | Example: 2/2/2007 | Example: Ben Brannon
2 | Example: Iris 2 | Example: Backup of work progress - Basement Complete | Example: C:\... | Example: 3/6/2008 | Example: Ben Brannon
3 | Example: Iris 3 | Example: Backup of work progress - Bldg A L1 and L2 geometry complete | Example: C:\... | Example: 3/6/2008 | Example: Ben Brannon
4 | Example: Iris 4 | Example: Backup of work progress- Building A Geometry complete | Example: C:\... | Example: 3/9/2008 | Example: Ben Brannon
5 | Example: … | Example: … | Example: … | Example: … | Example: Ben Brannon
6
7
8
9
10
11
12
13
14
15

## Units
Input | Units & Filing Structure |  |  | Carbon Free Boston
Calculation |  |  |  | 259104-00
Notes
Model Units (Auto fills to other tabs) |  | Common Unit Conversions
Opaque Construction U-Value | hr-ft²-F/Btu (R-Value) | Divide | by | To Obtain
Slab-on-Grade U-Value / F-Factor | hr-ft²-F/Btu (R-Value) | Btu/hr-ft²-F | 0.1761 | W/m²-K
Glazing Construction U-Value | Btu/hr-ft²-F (U-Value) | SHGC | 0.87 | SC
Glazing Solar Heat Gain | SHGC | cfm/ft² | 0.19685 | L/s/m²
Infiltration / Air Permeability | ACH | ft² | 10.764 | m²
Occupant Density | (ft²/person) | ft | 3.28 | m
Occupant Heat Gain | (Btu/h/person) | Btu/h | 3.412 | W
Lighting & Equipment Heat Gains | (W/ft²) | gal | 0.26417 | liters
Process Loads | (W) | gpm | 15.8504 | L/s
Temperature | (°F) | cfm | 2.1189 | L/s
DHW Demand | (gal/person/day) | ft H2O | 2.3067 | psi
Occupant-Based Ventilation | (cfm/person) | ft H2O | 0.33456 | kPa
Area-Based Ventilation | (cfm/ft²) | Pa | 249 | in wg
Air Change Requirement | (ACH) | EER | 3.412 | COP
Area | (ft²) | kW | 3.5169 | tons
Airflow | cfm | Btu/h | 12000 | tons
Water flow | gpm | W | 746 | HP
Heating and Cooling Capacity | kBtu/h | To Obtain | by | Multiply
Temperature Conversion
Recommended Filing Structure [Link] |  | T(°C) = [T(°F) - 32] × 5/9
01 Correspondence Specific to Energy Modelling |  | T(°F) = T(°C) × 9/5 + 32
02 Calculation Plan
03 Input Data
01 Weather Data
02 Zoning Diagram
03 Envelope Data
04 Lighting Data
05 Equipment and Other Internal Gains
06 Service Hot Water
07 Airside System Data
08 Waterside System Data
09 Utility Data
10 Special Systems
11 Equipment Submetering
04 Model Files
05 Results
06 Reference Documents
Opaque Construction Units
Btu/hr-ft²-F (U-Value)
hr-ft²-F/Btu (R-Value)
W/m²-K (U-Value)
m²-K/W (R-Value)
Slab-on-grade Units
Btu/hr-ft²-F (U-Value)
hr-ft²-F/Btu (R-Value)
Btu/hr-ft-F
W/m²-K (U-Value)
m²-K/W (R-Value)
W/m-K
Solar Heat Gain Units
SHGC
SC
G-Value
Infiltration / Air Permeability Units
(cfm/ft² facade)
(L/s/m² facade)
(cfm/ft² floor area)
(L/s/m² floor area)
ACH
(m³/h-m²)
Occupant Density Units
(ft²/person)
(people/1000 ft²)
(m²/person)
(people/100 m²)
(# of people)
Occupant Heat Gain Units
(Btu/h/person)
(W/person)
Internal Gain Units
(W/ft²)
(W/m²)
Process Load Units
(Btu/h)
(W)
(W/ft²)
(W/m²)
Temperature Units
(°F)
(°C)
DHW Demand Units
(gal/person/hour)
(gal/person/day)
(L/person/hour)
(L/person/day)
Occupant-Based Ventilation Units
(cfm/person)
(L/s/person)
Area-Based Ventilation Units
(cfm/ft²)
(L/s/m²)
(ACH)
Air-Change Requirements
(cfm)
(L/s)
(ACH)
Area
(ft²)
(m²)
Airflow
cfm
L/s
m³/s
Water Flow
gpm
L/min
Heating and Cooling Capacity
kBtu/h
kW

## Input Summary
Input | Input Summary | [7 empty] | Copy columns as needed for each model variant. Columns that have been superseded may be hidden. |  |  |  |  | Copy columns as needed for each model variant. Columns that have been superseded may be hidden. | Carbon Free Boston
Calculation | [14 empty] | 259104-00
Notes
[10 empty] | CBECS -1950, sample size: 7 | CBECS 1950-1980, sample size: 9 | CBECS 1980-2000, sample size: 8 | CBECS 2000-, sample size: 3
| Pre-1950 |  | 1950-1980 |  | 1980-2000 |  | Post-2000 |  | Source / Comments |  |  |  |  | For Further Discussion
Envelope
| Value | Units | Value | Units | Value | Units | Value | Units
Exterior Wall R-Value | [9 empty] | Wall construction material 43% Brick, stone, or stucco 57% Aluminum, asbestos, plastic, or wood materials (siding, shingles, tiles, or shakes) Exterior wall replacement Insulation upgrade 29% Yes | Wall construction material 56% Concrete block or poured concrete (above grade) 22% Brick, stone, or stucco 11% Aluminum, asbestos, plastic, or wood materials (siding, shingles, tiles, or shakes) 11% Sheet metal panels Exterior wall replacement Insulation upgrade 33% Yes | Wall construction material 12% Aluminum, asbestos, plastic, or wood materials (siding, shingles, tiles, or shakes) 62% Brick, stone, or stucco 25% Concrete block or poured concrete (above grade) Exterior wall replacement 12% Yes Insulation upgrade | Wall construction material 67% Brick, stone, or stucco 33% Sheet metal panels Exterior wall replacement Insulation upgrade
Mass Wall | 5 | hr-ft²-F/Btu (R-Value) | 6.4168 | hr-ft²-F/Btu (R-Value) | 9.9943 | hr-ft²-F/Btu (R-Value) | 8.14 | hr-ft²-F/Btu (R-Value) | Post-1950s - DOE reference model for standalone retail Pre-1950s - Assume brick wall (R-2.4) with no insulation. Assume no insulation upgrade.(CBECS) |  |  |  |  | Why is 1980-2000 u-value higher than post-2000?
Roof R-Value | 11 | hr-ft²-F/Btu (R-Value) | 14.1965 | hr-ft²-F/Btu (R-Value) | 15.6161 | hr-ft²-F/Btu (R-Value) | 16.18 | hr-ft²-F/Btu (R-Value) | Post-1950s - DOE reference model for standalone retail Pre-1950s - Assume Wood Framing (R-2.46) with no insulation. Assume 29% have been upgraded to 1980-2000 standard.(CBECS) | Roof construction material 29% Plastic, rubber, or synthetic sheeting (single or multiple ply) 14% Wood shingles, shakes, or other wooden materials 57% Asphalt, fiberglass, or other shingles Roof replacement 43% Yes | Roof replacement 56% Yes Roof construction material 56% Plastic, rubber, or synthetic sheeting (single or multiple ply) 11% Built-up (tar, felts, or fiberglass and a ballast, such as stone) 22% Asphalt, fiberglass, or other shingles 11% Metal surfacing | Roof replacement 25% Yes Roof construction material 50% Plastic, rubber, or synthetic sheeting (single or multiple ply) 12% Built-up (tar, felts, or fiberglass and a ballast, such as stone) 12% Asphalt, fiberglass, or other shingles 25% Metal surfacing | Roof construction material 33% Plastic, rubber, or synthetic sheeting (single or multiple ply) 33% Concrete 33% Metal surfacing Roof replacement
Floor: Slab-on-grade R-Value / F-Factor | 1.8171 | hr-ft²-F/Btu (R-Value) | 1.8171 | hr-ft²-F/Btu (R-Value) | 1.8171 | hr-ft²-F/Btu (R-Value) | 1.82 | hr-ft²-F/Btu (R-Value) | Post-1950s - DOE reference model for standalone retail Pre-1950s - assume same as post-1950
Underground Walls R-Value | N/A | hr-ft²-F/Btu (R-Value) | N/A | hr-ft²-F/Btu (R-Value) | N/A | hr-ft²-F/Btu (R-Value) | N/A | hr-ft²-F/Btu (R-Value) | Post-1950s - DOE reference model for standalone retail Pre-1950s - assume same as post-1950
Window to Wall Ratio | 7.1 | % | 7.1 | % | 7.1 | % | 7.1 | % | Post-1950s - DOE reference model for standalone retail Pre-1950s - assume same as post-1950 | Percent exterior glass 14% 26 to 50 percent 29% 11 to 25 percent 29% 2 to 10 percent 14% 1 percent or less | Percent exterior glass 22% 2 to 10 percent 33% 11 to 25 percent 11% 51 to 75 percent 11% 1 percent or less 11% 26 to 50 percent | Percent exterior glass 12% 1 percent or less 25% 26 to 50 percent 62% 2 to 10 percent | Percent exterior glass 33% 11 to 25 percent 33% 2 to 10 percent 33% 1 percent or less
Glazing Assembly R-Value | [9 empty] | Window replacement 43% Yes Tinted window glass 14% Yes Window glass type 43% Single layer glass 57% Combination of both | Window replacement 22% Yes Tinted window glass 78% Yes Window glass type 78% Combination of both 22% Single layer glass | Window replacement 12% Yes Tinted window glass 50% Yes Window glass type 62% Combination of both 38% Multi-layer glass | Window replacement Tinted window glass 33% Yes Window glass type 67% Combination of both 33% Multi-layer glass
Windows | 0.6551 | Btu/hr-ft²-F (U-Value) | 0.6217 | Btu/hr-ft²-F (U-Value) | 0.59 | Btu/hr-ft²-F (U-Value) | 0.57 | Btu/hr-ft²-F (U-Value) | Post-1950s - DOE reference model for standalone retail Pre-1950s - Slightly worse performance than 1950-1980. (More single pane windows that 1950-1980 (CBECS)).
Glazing Assembly Solar Heat Gain
Windows | 0.43103 | SHGC | 0.41 | SHGC | 0.39 | SHGC | 0.39 | SHGC | Post-1950s - DOE reference model for standalone retail Pre-1950s - Slightly worse performance than 1950-1980. (More single pane windows that 1950-1980 (CBECS)).
Glazing Assembly VLT
Windows | 33.03% | % | 32% | % | 31% | % | 31% | % | Post-1950s - DOE reference model for standalone retail Pre-1950s - Slightly higher VLT than 1950-1980. (More single pane windows that 1950-1980 (CBECS)).
Skylight to Roof Ratio | N/A | % | N/A | % | N/A | % | N/A | % | DOE reference model for standalone retail
Skylight U-Value | N/A | Btu/hr-ft²-F (U-Value) | N/A | Btu/hr-ft²-F (U-Value) | N/A | Btu/hr-ft²-F (U-Value) | N/A | Btu/hr-ft²-F (U-Value)
Skylight Solar Heat Gain | N/A | SHGC | N/A | SHGC | N/A | SHGC | N/A | SHGC
Skylight VLT | N/A | % | N/A | % | N/A | % | N/A | %
Local Shading Devices | None |  | None |  | None |  | None |  |  | External overhangs or awnings 57% Yes | External overhangs or awnings 78% Yes | External overhangs or awnings 75% Yes | External overhangs or awnings 33% Yes
Infiltration / Air Permeability | 0.405 |  | 0.27 | ACH | 1.01 | ACH | 0.27 | ACH | Post-1950- DOE reference model Pre-1950s- Assume 50% increase compared to 1950-1980.
Occupancy
Occupant Density | Space Type | Occupant Density | Space Type | Occupant Density | Space Type | Occupant Density | Space Type | Occupant Density |  | Occupancy (Individual Variables) Number of employees avg: 0.0007915194346289752 per sqft | Occupancy (Individual Variables) Number of employees avg: 0.0008375401560348784 per sqft | Occupancy (Individual Variables) Number of employees avg: 0.0007337707182320442 per sqft | Occupancy (Individual Variables) Number of employees avg: 0.0007323780576060211 per sqft
|  | (ft²/person) |  | (ft²/person) |  | (ft²/person) |  | (ft²/person) | DOE reference model for standalone retail
| Back_Space | 300 | Back_Space | 300 | Back_Space | 300 | Back_Space | 300
| Core_Retail | 67 | Core_Retail | 67 | Core_Retail | 67 | Core_Retail | 67
| Point_Of_Sale | 67 | Point_Of_Sale | 67 | Point_Of_Sale | 67 | Point_Of_Sale | 67
| Front_Retail | 67 | Front_Retail | 67 | Front_Retail | 67 | Front_Retail | 67
| Front_Entry | 67 | Front_Entry | 67 | Front_Entry | 67 | Front_Entry | 67
Lighting & Receptacles
Interior Lighting Power Density | Space Type | Lighting Power Density | Space Type | Lighting Power Density | Space Type | Lighting Power Density | Space Type | Lighting Power Density |  | Lighting type Light-emitting diode (LED) bulbs 29% Yes Incandescent bulbs 57% Yes Fluorescent bulbs 100% Yes High intensity discharge (HID) bulbs 14% Yes Halogen bulbs 57% Yes Compact fluorescent bulbs 86% Yes Lighting upgrade 29% Yes | Lighting type Light-emitting diode (LED) bulbs 44% Yes Incandescent bulbs 56% Yes Fluorescent bulbs 100% Yes High intensity discharge (HID) bulbs 33% Yes Halogen bulbs 33% Yes Compact fluorescent bulbs 89% Yes Other type of bulbs 11% Yes Lighting upgrade 56% Yes | Lighting type Light-emitting diode (LED) bulbs 50% Yes Incandescent bulbs 50% Yes Fluorescent bulbs 88% Yes High intensity discharge (HID) bulbs 38% Yes Halogen bulbs 38% Yes Compact fluorescent bulbs 50% Yes Lighting upgrade 25% Yes | Lighting type Light-emitting diode (LED) bulbs 33% Yes Incandescent bulbs 33% Yes Fluorescent bulbs 67% Yes High intensity discharge (HID) bulbs 33% Yes Halogen bulbs 33% Yes Compact fluorescent bulbs 67% Yes Other type of bulbs 33% Yes Lighting upgrade 33% Yes
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²) | Post-1950s - DOE reference model for standalone retail Pre-1950s - CBECS mostly fluorescent, incandescent and halogen. Assume same as 1950-1980
| Back_Space | 5 | Back_Space | 5 | Back_Space | 5 | Back_Space | 5
| Core_Retail | 8 | Core_Retail | 10 | Core_Retail | 10 | Core_Retail | 10 | [5 empty] | Should post-2000 LPDs be so much lower than pre-2000?
| Point_Of_Sale | 8 | Point_Of_Sale | 10 | Point_Of_Sale | 10 | Point_Of_Sale | 10
| Front_Retail | 8 | Front_Retail | 10 | Front_Retail | 10 | Front_Retail | 10
| Front_Entry | 8 | Front_Entry | 10 | Front_Entry | 10 | Front_Entry | 10
Daylighting Controls | None |  | None |  | None |  | None
Other Lighting Control Credits | Scheduled shutoff |  | None |  | None |  | None |  | Post-1950s - DOE reference model for standalone retail Pre-1950s - CBECS- occupancy sensors and light scheduling | Lighting controls Multi-level lighting or dimming 29% Yes Occupancy sensors 29% Yes Light scheduling 57% Yes | Lighting controls Multi-level lighting or dimming 44% Yes BAS controls lighting 33% Yes Occupancy sensors 56% Yes Light scheduling 44% Yes | Lighting controls Multi-level lighting or dimming 25% Yes BAS controls lighting 38% Yes Occupancy sensors 50% Yes Light scheduling 75% Yes Daylight harvesting 25% Yes | Lighting controls Multi-level lighting or dimming 33% Yes BAS controls lighting 67% Yes Occupancy sensors 33% Yes Light scheduling 67% Yes Daylight harvesting 33% Yes | No controls in DOE reference model, but CBECS data indicates dimming, occ sensors and scheduled shutoff. Should lighting controls be modeled across all building vintages? If not, remove from pre-1950 for consistency.
External / Site Lighting Power (W) | Exterior Lighting | 9995 | Exterior Lighting | 9995 | Exterior Lighting | 9995 | Exterior Lighting | 8266 | DOE reference model for standalone retail
Receptacle Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density |  | Plug loads (Individual Variables) Number of ice makers avg: 0.0002631578947368421 per sqft Number of closed case refrigeration units avg: 0.0013157894736842105 per sqft Number of refrigerated vending machines avg: 0.0002631578947368421 per sqft Number of walk-in units avg: 0.0002631578947368421 per sqft Number of residential refrigerators avg: 0.0005164319248826291 per sqft Number of computers avg: 0.000480565371024735 per sqft Number of compact refrigerators avg: 0.00037037037037037035 per sqft Plug load control 14% Yes Number of open case refrigeration units avg: 0.0005263157894736842 per sqft Electrical upgrade 43% Yes | Plug loads (Individual Variables) Number of ice makers avg: 1.7789072426937737e-05 per sqft Number of closed case refrigeration units avg: 0.00021222193812324213 per sqft Number of refrigerated vending machines avg: 5.2356020942408376e-05 per sqft Number of residential refrigerators avg: 4.515805318615153e-05 per sqft Number of computers avg: 0.0002618657937806874 per sqft Number of compact refrigerators avg: 0.00010103439980755353 per sqft Number of walk-in units avg: 7.398273736128237e-05 per sqft Number of open case refrigeration units avg: 0.00014993646759847522 per sqft Electrical upgrade 56% Yes | Plug loads (Individual Variables) Number of ice makers avg: 1.2760527435133986e-05 per sqft Number of closed case refrigeration units avg: 0.00014809329877823029 per sqft Number of refrigerated vending machines avg: 4.127579737335835e-05 per sqft Number of residential refrigerators avg: 3.4530386740331494e-05 per sqft Number of computers avg: 0.0002779696132596685 per sqft Number of compact refrigerators avg: 4.6222222222222224e-05 per sqft Number of walk-in units avg: 3.9984006397441024e-05 per sqft Number of open case refrigeration units avg: 0.00012095032397408207 per sqft Electrical upgrade 12% Yes | Plug loads (Individual Variables) Number of ice makers avg: 3.3333333333333335e-05 per sqft Number of closed case refrigeration units avg: 0.00021818181818181818 per sqft Number of refrigerated vending machines avg: 3.6363636363636364e-05 per sqft Number of residential refrigerators avg: 6.666666666666667e-05 per sqft Plug load control 33% Yes Number of computers avg: 0.00018128654970760234 per sqft Number of compact refrigerators avg: 6.363636363636364e-05 per sqft Number of walk-in units avg: 8.187134502923976e-05 per sqft Number of open case refrigeration units avg: 0.00017878787878787878 per sqft Electrical upgrade 33% Yes
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²) | DOE reference model for standalone retail
| Back_Space | 1.5 | Back_Space | 1.5 | Back_Space | 1.5 | Back_Space | 1.5
| Core_Retail | 1 | Core_Retail | 1 | Core_Retail | 1 | Core_Retail | 1
| Point_Of_Sale | 2 | Point_Of_Sale | 2.5 | Point_Of_Sale | 2.5 | Point_Of_Sale | 2.5
| Front_Retail | 1 | Front_Retail | 1 | Front_Retail | 1 | Front_Retail | 1
| Front_Entry | 1 | Front_Entry | 1 | Front_Entry | 1 | Front_Entry | 1
Gas Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²) | Post 1950s- DOE reference model Pre-1950s- no data, assume same as post-1950
| Core_Retail | 0 | Core_Retail | 0 | Core_Retail | 0 | Core_Retail | 0
Process Loads | Process Load Type | Equipment Load | Process Load Type | Equipment Load | Process Load Type | Equipment Load | Process Load Type | Equipment Load |  | Cooking fuel source Propane used for cooking 29% Yes Electricity used for cooking 14% Yes Process load (Individual Variables) Number of servers avg: 9.389671361502347e-05 per sqft Manufacturing fuel source Propane used for manufacturing 14% Yes Electricity used for manufacturing 29% Yes | Cooking fuel source Electricity used for cooking 44% Yes Natural gas used for cooking 33% Yes District steam used for cooking 11% Yes Process load (Individual Variables) Number of servers avg: 4.870920603994155e-05 per sqft Manufacturing fuel source | Cooking fuel source Electricity used for cooking 12% Yes Natural gas used for cooking 25% Yes Process load (Individual Variables) Elevators 12% Yes Number of servers avg: 4.285448108813117e-05 per sqft Manufacturing fuel source Electricity used for manufacturing 25% Yes Natural gas used for manufacturing 12% Yes | Cooking fuel source Propane used for cooking 33% Yes Electricity used for cooking 33% Yes Natural gas used for cooking 33% Yes Process load (Individual Variables) Number of servers avg: 4.242424242424242e-05 per sqft Manufacturing fuel source
|  | (W) |  | (W) |  | (W) |  | (W) | DOE reference model for standalone retail
| N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Schedules | [8 empty] | Post-1950s - DOE reference model for standalone retail Pre-1950s - CBECS
Internal Gain Schedules | Space Type | Schedule | Space Type | Schedule | Space Type | Schedule | Space Type | Schedule | DOE reference model for standalone retail
| Back_Space | BLDG_OCC_SCH | Back_Space | BLDG_OCC_SCH | Back_Space | BLDG_OCC_SCH | Back_Space | BLDG_OCC_SCH
| Core_Retail | BLDG_OCC_SCH | Core_Retail | BLDG_OCC_SCH | Core_Retail | BLDG_OCC_SCH | Core_Retail | BLDG_OCC_SCH
| Point_Of_Sale | BLDG_OCC_SCH | Point_Of_Sale | BLDG_OCC_SCH | Point_Of_Sale | BLDG_OCC_SCH | Point_Of_Sale | BLDG_OCC_SCH
| Front_Retail | BLDG_OCC_SCH | Front_Retail | BLDG_OCC_SCH | Front_Retail | BLDG_OCC_SCH | Front_Retail | BLDG_OCC_SCH
| Front_Entry | BLDG_OCC_SCH | Front_Entry | BLDG_OCC_SCH | Front_Entry | BLDG_OCC_SCH | Front_Entry | BLDG_OCC_SCH
| #REF! | Example: Lobby |  |  |  |  | #REF! | Example: Lobby
| #REF! | Example: Kitchen |  |  |  |  | #REF! | Example: Kitchen
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Kitchen |  |  |  |  | #REF! | Example: Kitchen
| #REF! | Example: Lobby |  |  |  |  | #REF! | Example: Lobby
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | Example: Office |  |  |  |  | #REF! | Example: Office
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
| #REF! | [5 empty] | #REF!
Process Load Schedules | Process Load Type | Schedule | Process Load Type | Schedule | Process Load Type | Schedule | Process Load Type | Schedule | DOE reference model for standalone retail
| N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Building Hours of Operation | Occupied 8 am to 10 pm, varying throughout the day |  | Occupied 8 am to 10 pm, varying throughout the day |  | Occupied 8 am to 10 pm, varying throughout the day |  | Occupied 8 am to 10 pm, varying throughout the day
HVAC Airside | [8 empty] | Post-1950s - DOE reference model for standalone retail Pre-1950s - CBECS
Primary HVAC System Type - Dominant space type | Residential type central AC with DX cooling and gas furnace, constant volume |  | Packaged single zone rooftop DX units with gas furnace, constant volume |  | Packaged single zone rooftop DX units with gas furnace, constant volume |  | Packaged single zone rooftop DX units with gas furnace, constant volume |  | Post-1950s - DOE reference model for standalone retail Pre-1950s - CBECS | Heating ventilation type Heating ventilation: Central air handling with VAV 14% Yes Heating ventilation: Central air handling with CAV 43% Yes Cooling ventilation type Cooling ventilation: Central air-handling unit with CAV 43% Yes Cooling ventilation: Central air-handling unit with VAV 14% Yes Main heating equipment 29% Boilers inside (or adjacent to) the building that produce steam or hot water 29% Furnaces that heat air directly, without using steam or hot water 14% District steam or hot water piped in from outside the building 29% Packaged central unit (roof mounted) HVAC equipment upgrade 29% Yes | HVAC equipment upgrade 56% Yes Heating ventilation type Heating ventilation: Central air handling with VAV 33% Yes Heating ventilation: Demand controlled ventilation 22% Yes Heating ventilation: Central air handling with CAV 67% Yes Cooling ventilation type Cooling ventilation: Central air-handling unit with CAV 78% Yes Cooling ventilation: Demand controlled ventilation 11% Yes Cooling ventilation: Central air-handling unit with VAV 33% Yes Main heating equipment 11% District steam or hot water piped in from outside the building 11% Individual space heaters (other than heat pumps) 67% Packaged central unit (roof mounted) 11% Heat pumps (other than components of a packaged unit) | HVAC equipment upgrade 38% Yes Heating ventilation type Heating ventilation: Central air handling with VAV 12% Yes Heating ventilation: Central air handling with CAV 88% Yes Cooling ventilation type Cooling ventilation: Central air-handling unit with CAV 75% Yes Cooling ventilation: Central air-handling unit with VAV 38% Yes Main heating equipment 12% Individual space heaters (other than heat pumps) 12% Furnaces that heat air directly, without using steam or hot water 75% Packaged central unit (roof mounted) | HVAC equipment upgrade 33% Yes Heating ventilation type Heating ventilation: Dedicated outside air system 33% Yes Heating ventilation: Central air handling with CAV 33% Yes Cooling ventilation type Cooling ventilation: Dedicated outside air system 33% Yes Cooling ventilation: Central air-handling unit with CAV 33% Yes Cooling ventilation: Central air-handling unit with VAV 33% Yes Main heating equipment 33% Boilers inside (or adjacent to) the building that produce steam or hot water 67% Packaged central unit (roof mounted) | Change system type for post-1950 vintages? CBECS suggests packaged central airhandlers with CAV.
Other HVAC System Type(s) | N/A |  | Front_Entry- standalone gas furnace |  | Front_Entry- standalone gas furnace |  | Front_Entry- standalone gas furnace |  | Post-1950s - DOE reference model for standalone retail Pre-1950s - CBECS
System Parameters and Controls (Economizer, DCV, energy recovery, etc.) | Temperature controlled via programmable thermostat |  | Differential drybulb economizer |  | Differential drybulb economizer |  | Differential drybulb economizer |  | Post-1950s - DOE reference model for standalone retail Pre-1950s - CBECS | How reduce cooling 14% Manually shut down equipment 14% Manually change thermostat 43% Programmable thermostat Economizer cycle 29% Yes How reduce heating 29% Manually change thermostat 57% Programmable thermostat | How reduce cooling 22% Manually shut down equipment 22% Part of the Building Automation System 33% Manually change thermostat Economizer cycle 22% Yes How reduce heating 22% Manually shut down equipment 22% Part of the Building Automation System 56% Manually change thermostat | How reduce cooling 12% Manually change thermostat 38% Part of the Building Automation System 50% Programmable thermostat Economizer cycle 38% Yes How reduce heating 12% Manually change thermostat 38% Part of the Building Automation System 50% Programmable thermostat | How reduce cooling 67% Part of the Building Automation System Economizer cycle 33% Yes How reduce heating 67% Part of the Building Automation System 33% Manually shut down equipment
HVAC Waterside
Cooling Source Parameters | Packaged AC, COP = 2.84 |  | Packaged DX, COP = 3.23 |  | Packaged DX, COP = 3.23 |  | Packaged DX, COP = 3.5 |  | Post-1950s - DOE reference model for standalone retail Pre-1950s - CBECS, main cooling replaced in most stores. Assume compliance with ASHRAE 90.1-2004 | Main cooling replaced 86% Yes Cooling fuel source Electricity used for cooling 86% Yes | Main cooling replaced 56% Yes Cooling fuel source Electricity used for cooling 78% Yes | Main cooling replaced 38% Yes Chiller type Chiller type: Air-cooled 12% Yes Cooling fuel source Electricity used for cooling 100% Yes Natural gas used for cooling 12% Yes | Cooling fuel source Electricity used for cooling 67% Yes
Chilled Water Loop & Pump Parameters | N/A |  | N/A |  | N/A |  | . |  | Post-1950s - DOE reference model for standalone retail Pre-1950s - CBECS
Condenser Water Loop & Pump Parameters | N/A |  | N/A |  | N/A |  | N/A |  | Post-1950s - DOE reference model for standalone retail Pre-1950s - CBECS
Cooling tower Parameters | N/A |  | N/A |  | N/A |  | N/A |  | Post-1950s - DOE reference model for standalone retail Pre-1950s - CBECS
Heating Source Parameters | Fuel oil furnace, AFUE = 78% |  | Gas furnace, efficiency = 78% |  | Gas furnace, efficiency = 78% |  | Gas furnace, efficiency = 80% |  | Post-1950s - DOE reference model for standalone retail Pre-1950s - CBECS, equally split between furnace, packaged RTU and boiler. 57% of main heating replaced- assume compliance with ASHRAE-90.1 2004 | Heating fuel source District steam used for main heating 14% Yes Fuel oil used for main heating 43% Yes Propane used for main heating 29% Yes Electricity used for main heating 14% Yes Main heating replaced 57% Yes | Heating fuel source District steam used for main heating 11% Yes Fuel oil used for main heating 22% Yes Natural gas used for main heating 56% Yes Wood used for main heating 11% Yes Main heating replaced 67% Yes | Heating fuel source Fuel oil used for main heating 12% Yes Natural gas used for main heating 62% Yes Propane used for main heating 12% Yes Electricity used for main heating 12% Yes Main heating replaced 25% Yes | Heating fuel source Natural gas used for main heating 33% Yes Electricity used for main heating 33% Yes Wood used for main heating 33% Yes | Should packaged RTU, furnace, or boiler be used for pre-1950s? All represented equally in CBECS data.
Hot Water Loop & Pump Parameters | N/A |  | N/A |  | N/A |  | N/A |  | Post-1950s - DOE reference model for standalone retail Pre-1950s - CBECS
Service Hot Water
Domestic Hot Water System Parameters | N/A |  | N/A |  | N/A |  | N/A |  | Post-1950s - DOE reference model for standalone retail Pre-1950s - CBECS | DHW fuel source Electricity used for water heating 57% Yes Propane used for water heating 43% Yes Fuel oil used for water heating 14% Yes DHW heater type Booster water heaters avg: 0.0002631578947368421 per sqft Plumbing system upgrade 29% Yes | Plumbing system upgrade 44% Yes DHW fuel source Electricity used for water heating 89% Yes Natural gas used for water heating 44% Yes DHW heater type Booster water heaters avg: 3.5714285714285714e-06 per sqft | Plumbing system upgrade DHW fuel source Electricity used for water heating 88% Yes Natural gas used for water heating 50% Yes DHW heater type Booster water heaters avg: 0 per sqft | DHW fuel source Electricity used for water heating 67% Yes Natural gas used for water heating 33% Yes Plumbing system upgrade 33% Yes DHW heater type Booster water heaters avg: 9.090909090909091e-06 per sqft
Renewable Energy Systems
Renewable Energy System Description and Parameters | N/A |  | N/A |  | N/A |  | N/A |  | DOE reference model for standalone retail
General Notes
Notes

## Pre-1950 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [15 empty] | HVAC Parameters | [11 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/person/day) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Back_Space | Y | Occupied M-F, 7 am to 10 pm | 72 | 72 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.14764 | 0 | 0.37388 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 2.1 |  |  | 78%
Core_Retail | Y | Occupied M-F, 7 am to 10 pm | 72 | 72 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.29528 | 0 | 0.2182 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 2.1 |  |  | 78%
Point_Of_Sale | Y | Occupied M-F, 7 am to 10 pm | 72 | 72 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.29528 | 0 | 0.40297 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 2.1 |  |  | 78%
Front_Retail | Y | Occupied M-F, 7 am to 10 pm | 72 | 72 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.29528 | 0 | 0.40297 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 2.1 |  |  | 78%
Front_Entry | Y | Occupied M-F, 7 am to 10 pm | 72 | 72 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0 | 0 | 1 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 2.1 |  |  | 78%

## 1950-1980 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [15 empty] | HVAC Parameters | [11 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/person/day) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Back_Space | Y | Occupied M-F, 7 am to 10 pm | 65 | 65 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.14764 | 0 | 0.37388 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 2.5 |  |  | 78%
Core_Retail | Y | Occupied M-F, 7 am to 10 pm | 65 | 65 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.29528 | 0 | 0.2182 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 2.5 |  |  | 78%
Point_Of_Sale | Y | Occupied M-F, 7 am to 10 pm | 65 | 65 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.29528 | 0 | 0.40297 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 2.5 |  |  | 78%
Front_Retail | Y | Occupied M-F, 7 am to 10 pm | 65 | 65 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.29528 | 0 | 0.40297 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 2.5 |  |  | 78%
Front_Entry | Y | Occupied M-F, 7 am to 10 pm | 65 | 65 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0 | 0 | 1 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 2.5 |  |  | 78%

## 1980-2000 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [15 empty] | HVAC Parameters | [11 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/person/day) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Back_Space | Y | Occupied M-F, 7 am to 10 pm | 65 | 65 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.14764 | 0 | 0.37388 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 2.8 |  |  | 78%
Core_Retail | Y | Occupied M-F, 7 am to 10 pm | 65 | 65 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.29528 | 0 | 0.2182 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 2.8 |  |  | 78%
Point_Of_Sale | Y | Occupied M-F, 7 am to 10 pm | 65 | 65 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.29528 | 0 | 0.40297 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 2.8 |  |  | 78%
Front_Retail | Y | Occupied M-F, 7 am to 10 pm | 65 | 65 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.29528 | 0 | 0.40297 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 2.8 |  |  | 78%
Front_Entry | Y | Occupied M-F, 7 am to 10 pm | 65 | 65 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0 | 0 | 1 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 2.8 |  |  | 78%

## Post-2000 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [15 empty] | HVAC Parameters | [11 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/person/day) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Back_Space | Y | Occupied M-F, 7 am to 10 pm | 72 | 72 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.14764 | 0 | 0.37388 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.33 |  |  | 78%
Core_Retail | Y | Occupied M-F, 7 am to 10 pm | 72 | 72 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.29528 | 0 | 0.2182 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.33 |  |  | 78%
Point_Of_Sale | Y | Occupied M-F, 7 am to 10 pm | 72 | 72 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.29528 | 0 | 0.40297 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.33 |  |  | 78%
Front_Retail | Y | Occupied M-F, 7 am to 10 pm | 72 | 72 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0.29528 | 0 | 0.40297 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.33 |  |  | 78%
Front_Entry | Y | Occupied M-F, 7 am to 10 pm | 72 | 72 | 75.2 | 80 | N/A | N/A | 0 | 0 | 0 | 0 | 1 | N | N/A | UnitarySingle |  | Unitary | Gas |  |  | 3.33 |  |  | 78%

## Pre-1950 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Retail | Retail | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | DOE post1980 Reference Energy Model, Chicago
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Retail | Retail | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | DOE post1980 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Retail | Retail | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15
|  | Sun/Holiday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Elevator | Elevator | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | DOE Pre-1980 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## 1950-1980 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Retail | Retail | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | DOE post1980 Reference Energy Model, Chicago
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Retail | Retail | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | DOE post1980 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Retail | Retail | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | DOE post1980 Reference Energy Model, Chicago
|  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15
|  | Sun/Holiday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## 1980-2000 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Retail | Retail | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | DOE post1980 Reference Energy Model, Chicago
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Retail | Retail | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | DOE post1980 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Retail | Retail | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | DOE post1980 Reference Energy Model, Chicago
|  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15
|  | Sun/Holiday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## Post-2000 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Retail | Retail | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | DOE post1980 Reference Energy Model, Chicago
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Retail | Retail | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | DOE post1980 Reference Energy Model, Chicago
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Retail | Retail | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | DOE post1980 Reference Energy Model, Chicago
|  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15
|  | Sun/Holiday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday
Process Loads - |  | Weekday
Sat
Sun/Holiday

## Review
Input | Review |  |  |  | Carbon Free Boston |  | Notes:
Calculation |  |  |  |  | 259104-00 |  | - Create a copy of the Review tab for each model review
Notes | [6 empty] | - The reviewer should review the model itself, and not rely on what is documented in the Calc Plan
[5 empty] | Modeller | Reviewer
Reviewed by:
Date of review:
Review type:
Project Information (section to be filled out by modeller prior to review)
Project phase & modelling protocol: | Example: 100% Design Development, ASHRAE 90.1-2010 proposed and baseline model
Link to archived model file:
Link to zoning diagram:
Link to relevant drawing set:
Link to current results:
Link to energy model report:
Self-review of model is complete (Column G) |  | If "No", please indicate why self-review has not been performed:
Questions for reviewer and/or comments about model
Model Metrics | Proposed | Baseline | Benchmark (if known) | Units
Energy Use Intensity (EUI) |  |  |  | kBtu/ft²/year
Heating Plant Capacity |  |  |  | Btu/ft²
Cooling Plant Capacity |  |  |  | ft²/ton
Total Design Supply Airflow |  |  |  | cfm/ft²
Total Outdoor Airflow |  |  |  | cfm/ft²
Documentation and file storage
Inputs documented in this workbook or elsewhere
Files archived and saved in appropriate location on network
Detailed calculations (in support of input values) are documented and saved
Comments
Weather
Appropriate and correct weather file is used. A copy is saved on the network in the "Weather Data" folder.
Climate zone is correct for project location
Appropriate and correct Design Day data is used (check against Basis of Design report)
Comments
Geometry and Shading
Building compass orientation is correct
Building elevation above sea level is correct
Overhangs and/or other shading devices, or site shading, if modelled, are correctly configured in the software
Comments
Zoning
The number of zones in the model is appropriate for the desired level of analysis. Rooms of a similar type and internal load density with the same exposure may be zoned together.
Zoning is the same between model variants, unless variation is justified by an evaluated measure
Comments
Envelope and Construction
Window to gross wall ratio seems reasonable for the building and matches design drawings
Construction types are correctly assigned to proposed and baseline models
Window U-values, SHGC/G-values, and VLT are whole-assembly values (including framing impacts) and are input as required by the software
Opaque U-values are whole-assembly values and are input as required by the software. Insulation values of steel or wood-framed walls are appropriately de-rated in accordance with ASHRAE Appendix A or other reference standard.
U-values of horizontal constructions and glazing are derated for horizontal convection (U-values should be worse than vertical assemblies)
For natural ventilation models: window opening sizes, opening positions and the ventilation methodology are correct
Model accounts for an appropriate level of thermal mass. (Check that construction layer build-up reasonably matches design, or room mass settings are appropriate for the building construction type.)
Modelled infiltration rates are reasonable and identical between model variants, unless modification is justified for a measure evaluation
Comments
Internal Loads
Interior lighting power densities are reasonable given the building use(s)
Decorative lighting is accounted for in lighting power density values or separately, as appropriate
Daylight control is included where appropriate
Credit is taken for reduced lighting power due to occupancy sensors where appropriate
Receptacle loads and occupant densities are the same for all model variants, unless modification is justified for a measure evaluation
Peak and scheduled equipment loads represent anticipated actual draws from the equipment rather than nameplate values
Electrical room: entire building switchgear capacity is not assigned as an electric load
Comments
Schedules
Schedules are the same for all model variants, unless modification is justified for a measure evaluation
Internal load schedules set the load to 100% on for the cooling design condition and 100% off for the heating design condition
Internal gain schedules vary throughout the day appropriately
Schedules used are reasonable (i.e. taken from a reference standard, and/or informed by conversation with building owner)
Any continuous loads have an appropriate schedule applied (e.g. escalators, process equipment)
Elevator schedule is included, if applicable
Exterior lighting schedule or photocell control is included, if applicable
Comments
Space Conditioning
All conditioned zones are assigned to HVAC systems
Any included unconditioned zones are set to be unconditioned in the model
Thermostat setpoints and driftpoints are correct
Comments
Airside Systems
Airside systems reasonably approximate the designed systems
Supply air temperatures and control strategies (e.g. SAT reset, economizer control) match the proposed design and baseline requirements
System schedules are consistent with design (e.g. fan schedules align with occupancy schedules such that the HVAC systems are enabled during occupied hours)
Ventilation is included per the design intent. Ventilation rates meet applicable codes.
Ventilation design flow rates and schedules are identical between model variants unless modification is justified
Exhaust is properly accounted for within the capabilities of the software tool. Room exhaust is distinguished from system level exhaust.
Schedules set the ventilation flows to 100% for the heating and cooling design conditions
Ventilation is scheduled ON during occupied hours and OFF during unoccupied hours, or otherwise according to the design sequence of operation
Demand controlled ventilation is modelled if applicable
Proposed fan power is correctly modelled per the design brake horsepowers and motor efficiencies. Baseline fan power includes any applicable pressure drop adjustments. Any included return and exhaust fan power is accounted for.
Fan drives are modelled correctly as either variable or constant speed
Pressure drop across heat recovery devices is accounted for (and not double counted)
Comments
Waterside Systems and Plant Equipment
Equipment types and efficiencies match the proposed design and baseline requirements
Part-load curves are based on actual equipment data or reasonably approximate part-load performance
Capacity of heating and cooling plants is reasonable (check SF/capacity)
Pumps and heat rejection fans are modelled correctly as either variable or constant speed
Control of the plant equipment in the model reasonably approximates the design sequence of operations (e.g. boiler and chiller staging, loop temperatures and reset controls)
If packaged equipment is used, efficiencies of equipment are broken out into supply fan, condenser fan, and compressor
Domestic hot water has been included for both models, as appropriate
Comments
Utility Rates
Rates are included. They are the same for all model variants, unless modification is justified
If Peak and Off-Peak rates apply, they are correctly implemented
Utility rates change often. Documentation of the utility rate(s) used for the analysis has been saved with the model files.
Comments
Metrics Checks
Building predicted annual energy costs are reasonable
Building EUI (Energy Use Index, energy use per square foot) is relatively close to benchmarks for your building type. Refer to the BEM Toolkit for sources of benchmarking data.
Annual cooling and heating load profiles make sense
The HVAC systems effectively satisfy the building loads (i.e. any "unmet" load hours are acceptable for the analysis). If high unmet loads occur, investigate and revise the model to resolve any problems
Comments
Energy Results by End Use
Differences in energy used by end use category between model variants can be explained by actual measures
Fan and pump power differences between model variants are roughly proportional to cooling and heating differences
Correct and consistent units are used when reporting the energy results
Energy uses which should be the same between variant models (e.g. plug loads) are indeed the same
Percentage of energy used by various end uses is reasonable given the building use(s)
Comments
Review Close-Out
Do the results of the energy model make sense according to experiential expertise, engineering judgment, and rules of thumb? If not, review the results again after the modeller has addressed the review comments.
Comments
LEED Specific Review Items
LEED Minimum Energy Performance Calculator is complete and highlighted comments on the Performance Outputs tab have been addressed.
Modelled floor area and space types are consistent with information reported in PIf3: Occupant and Usage Data.
Modelled system parameters align with the mechanical schedules provided for PIf4: Schedule and Overview Documents.
Modelled outdoor airflow is consistent with design OA reported in IEQp1 62.1 Calculator and AHU schedules.
Outdoor air is modelled per the design in the proposed, and per Appendix G requirements in the baseline.
Whenever credit is taken for demand control ventilation in the Proposed Case, the outside air ventilation rates for the Baseline Case are modelled using minimum ASHRAE 62.1 rates.
Any exceptional calculations have been documented in the LEED Minimum Energy Performance Calculator and a supplemental detailed narrative has been provided.
Any LEED CIRs related to the project have been clearly referenced in the documentation.
Core & shell projects: Model follows LEED C&S Appendices guidance. All unfinished spaces are included and modelled identically in the baseline and proposed, unless tenant lease agreement requires improvement over baseline requirements.
Utility rates are sourced from the same place (either EIA rates or actual utility rates for the project).
District energy systems are modelled per the guidance in the reference manual (v4) or the Treatment of District and Campus Thermal Energy In LEED (v2009).
Tilted surfaces are correctly modelled as walls or roofs as defined by ASHRAE 90.1 (per 90.1-2010, roofs are horizontal or tilted at an angle of less than 60° from horizontal).
Answer Options
Yes
No
Unclear
N/A
Review Type
Condensed
Detailed
Note on B10: Condensed reviews are recommended for earlier project phases. Detailed reviews are recommended for later project phases and/or review of a beginner energy modeler's work.