## Project
Input | General Information |  |  |  | Carbon Free Boston | Whole Building Energy Modelling Calculation Plan
Calculation |  |  |  |  | 259104-00 | Date of last update: 8/28/2017
Notes | [5 empty] | By: Holly Lattin / Ben Brannon
Project Overview |  |  |  | Source/Comments
Project Name | Carbon Free Boston
Project Number | 259104-00
Project Description | Modeling of the building stock for the city of Boston and testing of carbon reduction policies.
Modelling Scope | Prototype models of 15 buildings with conceptual testing of ECMs
Software, Version | EnergyPlus v8.6
Project Start Date | 2017-12-01
Project Completion Date | 2018-08-01
General Data |  |  |  | Source/Comments
Project Vintage | Four vintages to be tested: Pre-1950, 1950-1980, 1980-2000, and post-2000
Principal Building Type | Convention/Assembly
Actual Floor Area (Gross)
Actual Floor Area (Net)
Modelled Floor Area (Gross)
Modelled Floor Area (Net)
Benchmark Site Energy Use Intensity (EUI)
Sustainability Targets | N/A
Codes & Standards |  |  |  | Source/Comments
Applicable Codes & Standards | Varies by vintage.
Energy Code Compliance Path | N/A
Geography |  |  |  | Source/Comments
Project Location | Boston, MA
Weather File | Boston-Logan Airport TMY3
Heating and Cooling Design Conditions | ASHRAE 1%/99%
Site Elevation | 20 ft.
Project Climate Zone(s) | ASHRAE CZ5A
Building Orientation | Varies.
Site Shading | Modeled with no shading.
Model Image
Utility rates |  |  |  | Source/Comments
Electricity Rate/Structure | Varies (Eversource and National Grid)
Natural Gas Rate/Structure | Varies
District Heating Rate/Structure
District Cooling Rate/Structure
Other Utility Rates
Carbon Emission Factors |  |  |  | Source/Comments
Electricity (grid-supplied)
Electricity (grid-displaced)
Natural Gas
Other Carbon Emission Factors
Record of Model Files /Runs
At a minimum, file locations should be documented here for each major project milestone.
| File Name | Description | File Reference Location | Date Created | Created By
1 | Example: Iris 1 | Example: Primary model, backups along the way stored at: | Example: \\global.arup.com\americas\Jobs\S-F\240000\245844-00\4 Internal Project Data\4-04 Calculations\Mech\Energy Modeling\Models | Example: 2/2/2007 | Example: Ben Brannon
2 | Example: Iris 2 | Example: Backup of work progress - Basement Complete | Example: C:\... | Example: 3/6/2008 | Example: Ben Brannon
3 | Example: Iris 3 | Example: Backup of work progress - Bldg A L1 and L2 geometry complete | Example: C:\... | Example: 3/6/2008 | Example: Ben Brannon
4 | Example: Iris 4 | Example: Backup of work progress- Building A Geometry complete | Example: C:\... | Example: 3/9/2008 | Example: Ben Brannon
5 | Example: … | Example: … | Example: … | Example: … | Example: Ben Brannon
6
7
8
9
10
11
12
13
14
15

## Units
Input | Units & Filing Structure |  |  | Carbon Free Boston
Calculation |  |  |  | 259104-00
Notes
Model Units (Auto fills to other tabs) |  | Common Unit Conversions
Opaque Construction U-Value | hr-ft²-F/Btu (R-Value) | Divide | by | To Obtain
Slab-on-Grade U-Value / F-Factor | hr-ft²-F/Btu (R-Value) | Btu/hr-ft²-F | 0.1761 | W/m²-K
Glazing Construction U-Value | Btu/hr-ft²-F (U-Value) | SHGC | 0.87 | SC
Glazing Solar Heat Gain | SHGC | cfm/ft² | 0.19685 | L/s/m²
Infiltration / Air Permeability | ACH | ft² | 10.764 | m²
Occupant Density | (ft²/person) | ft | 3.28 | m
Occupant Heat Gain | (Btu/h/person) | Btu/h | 3.412 | W
Lighting & Equipment Heat Gains | (W/ft²) | gal | 0.26417 | liters
Process Loads | (W/ft²) | gpm | 15.8504 | L/s
Temperature | (°F) | cfm | 2.1189 | L/s
DHW Demand | (gal/person/day) | ft H2O | 2.3067 | psi
Occupant-Based Ventilation | (cfm/person) | ft H2O | 0.33456 | kPa
Area-Based Ventilation | (cfm/ft²) | Pa | 249 | in wg
Air Change Requirement | (ACH) | EER | 3.412 | COP
Area | (ft²) | kW | 3.5169 | tons
Airflow | cfm | Btu/h | 12000 | tons
Water flow | gpm | W | 746 | HP
Heating and Cooling Capacity | kBtu/h | To Obtain | by | Multiply
Refrigeration | (W)
Temperature Conversion
Recommended Filing Structure [Link] |  | T(°C) = [T(°F) - 32] × 5/9
01 Correspondence Specific to Energy Modelling |  | T(°F) = T(°C) × 9/5 + 32
02 Calculation Plan
03 Input Data
01 Weather Data
02 Zoning Diagram
03 Envelope Data
04 Lighting Data
05 Equipment and Other Internal Gains
06 Service Hot Water
07 Airside System Data
08 Waterside System Data
09 Utility Data
10 Special Systems
11 Equipment Submetering
04 Model Files
05 Results
06 Reference Documents
Opaque Construction Units
Btu/hr-ft²-F (U-Value)
hr-ft²-F/Btu (R-Value)
W/m²-K (U-Value)
m²-K/W (R-Value)
Slab-on-grade Units
Btu/hr-ft²-F (U-Value)
hr-ft²-F/Btu (R-Value)
Btu/hr-ft-F
W/m²-K (U-Value)
m²-K/W (R-Value)
W/m-K
Solar Heat Gain Units
SHGC
SC
G-Value
Infiltration / Air Permeability Units
(cfm/ft² facade)
(L/s/m² facade)
(cfm/ft² floor area)
(L/s/m² floor area)
ACH
(m³/h-m²)
Occupant Density Units
(ft²/person)
(people/1000 ft²)
(m²/person)
(people/100 m²)
(# of people)
Occupant Heat Gain Units
(Btu/h/person)
(W/person)
Internal Gain Units
(W/ft²)
(W/m²)
Process Load Units
(Btu/h)
(W)
(W/ft²)
(W/m²)
Temperature Units
(°F)
(°C)
DHW Demand Units
(gal/person/hour)
(gal/person/day)
(L/person/hour)
(L/person/day)
Occupant-Based Ventilation Units
(cfm/person)
(L/s/person)
Area-Based Ventilation Units
(cfm/ft²)
(L/s/m²)
(ACH)
Air-Change Requirements
(cfm)
(L/s)
(ACH)
Area
(ft²)
(m²)
Airflow
cfm
L/s
m³/s
Water Flow
gpm
L/min
Heating and Cooling Capacity
kBtu/h
kW

## Input Summary
Input | Input Summary | [7 empty] | Copy columns as needed for each model variant. Columns that have been superseded may be hidden. |  |  |  |  | Copy columns as needed for each model variant. Columns that have been superseded may be hidden. | Carbon Free Boston
Calculation | [14 empty] | 259104-00
Notes
[10 empty] | CBECS -1950, sample size: 7 | CBECS 1950-1980, sample size: 4 | CBECS 1980-2000, sample size: 8 | CBECS 2000-, sample size: 11
| Pre-1950 |  | 1950-1980 |  | 1980-2000 |  | Post-2000 |  | Source / Comments |  |  |  |  | For Further Discussion
Envelope
| Value | Units | Value | Units | Value | Units | Value | Units
Exterior Wall R-Value | [9 empty] | Wall construction material 29% Brick, stone, or stucco 71% Aluminum, asbestos, plastic, or wood materials (siding, shingles, tiles, or shakes) Exterior wall replacement Insulation upgrade 14% Yes | Wall construction material 25% Aluminum, asbestos, plastic, or wood materials (siding, shingles, tiles, or shakes) 50% Brick, stone, or stucco 25% Concrete block or poured concrete (above grade) Exterior wall replacement Insulation upgrade | Wall construction material 12% Concrete block or poured concrete (above grade) 12% No one major type 50% Aluminum, asbestos, plastic, or wood materials (siding, shingles, tiles, or shakes) 25% Sheet metal panels Exterior wall replacement 12% Yes Insulation upgrade | Wall construction material 18% Concrete block or poured concrete (above grade) 73% Aluminum, asbestos, plastic, or wood materials (siding, shingles, tiles, or shakes) 9% Brick, stone, or stucco Exterior wall replacement Insulation upgrade
Mass Wall | 2.4 | hr-ft²-F/Btu (R-Value) | 6.41 | hr-ft²-F/Btu (R-Value) | 10 | hr-ft²-F/Btu (R-Value) | 8.14 | hr-ft²-F/Btu (R-Value) | Post-1950- Assume similar to DOE warehouse reference model Pre-1950s- Assume brick wall (R-2.4) with no insulation. No insulation upgrade reported.(CBECS)
Roof R-Value | 4.8008 | hr-ft²-F/Btu (R-Value) | 14.2 | hr-ft²-F/Btu (R-Value) | 19.18 | hr-ft²-F/Btu (R-Value) | 16.18 | hr-ft²-F/Btu (R-Value) | Post-1950- Assume similar to DOE warehouse reference model Pre-1950s- Assume Wood Framing (R-2.46) with no insulation. Assume 14% insulation upgrade to 1980-2000 standard.(CBECS) | Roof replacement 57% Yes Roof construction material 14% Built-up (tar, felts, or fiberglass and a ballast, such as stone) 43% Asphalt, fiberglass, or other shingles 43% Metal surfacing | Roof replacement 25% Yes Roof construction material 25% Plastic, rubber, or synthetic sheeting (single or multiple ply) 25% Built-up (tar, felts, or fiberglass and a ballast, such as stone) 25% Asphalt, fiberglass, or other shingles 25% Metal surfacing | Roof replacement 12% Yes Roof construction material 25% Plastic, rubber, or synthetic sheeting (single or multiple ply) 50% Asphalt, fiberglass, or other shingles 25% Metal surfacing | Roof construction material 18% Plastic, rubber, or synthetic sheeting (single or multiple ply) 9% Wood shingles, shakes, or other wooden materials 45% Asphalt, fiberglass, or other shingles 27% Metal surfacing Roof replacement
Floor: Slab-on-grade R-Value / F-Factor | 3.05 | hr-ft²-F/Btu (R-Value) | 3.05 | hr-ft²-F/Btu (R-Value) | 3.05 | hr-ft²-F/Btu (R-Value) | 3.05 | hr-ft²-F/Btu (R-Value) | Post-1950- Assume similar to DOE warehouse reference model Pre-1950s- assume same as post-1950
Underground Walls R-Value | 1.74 | hr-ft²-F/Btu (R-Value) | 1.74 | hr-ft²-F/Btu (R-Value) | 1.74 | hr-ft²-F/Btu (R-Value) | 1.74 | hr-ft²-F/Btu (R-Value) | Post-1950- Assume similar to DOE warehouse reference model Pre-1950s- assume same as post-1950
Window to Wall Ratio | 38% | % | 38% | % | 38% | % | 38% | % | Post-1950- Assume similar to DOE school reference model Pre-1950s- assume same as post-1950 | Percent exterior glass 14% 26 to 50 percent 29% 11 to 25 percent 57% 2 to 10 percent | Percent exterior glass 25% 26 to 50 percent 25% 11 to 25 percent 50% 2 to 10 percent | Percent exterior glass 50% 1 percent or less 38% 2 to 10 percent | Percent exterior glass 36% 11 to 25 percent 27% 26 to 50 percent 27% 2 to 10 percent 9% 1 percent or less | Consider reducing WWR (especially for earlier vintages).
Glazing Assembly R-Value | [9 empty] | Window replacement 29% Yes Tinted window glass 14% Yes Window glass type 43% Single layer glass 57% Multi-layer glass | Window replacement Tinted window glass 50% Yes Window glass type 100% Single layer glass | Window replacement Tinted window glass 12% Yes Window glass type 12% Combination of both 12% Single layer glass 75% Multi-layer glass | Window replacement Tinted window glass 27% Yes Window glass type 9% Combination of both 18% Single layer glass 73% Multi-layer glass
Windows | 0.62 | Btu/hr-ft²-F (U-Value) | 0.62 | Btu/hr-ft²-F (U-Value) | 0.59 | Btu/hr-ft²-F (U-Value) | 0.57 | Btu/hr-ft²-F (U-Value) | Post-1950- Assume similar to DOE warehouse reference model Pre-1950s- assume same as 1950-1980 (based on CBECS statistics)
Glazing Assembly Solar Heat Gain
Windows | 0.41 | SHGC | 0.41 | SHGC | 0.39 | SHGC | 0.39 | SHGC | Post-1950- Assume similar to DOE warehouse reference model Pre-1950s- assume same as 1950-1980 (based on CBECS statistics)
Glazing Assembly VLT
Windows | 32% | % | 32% | % | 31% | % | 31% | % | Post-1950- Assume similar to DOE warehouse reference model Pre-1950s- assume same as 1950-1980 (based on CBECS statistics)
Skylight to Roof Ratio | N/A | % | N/A | % | N/A | % | N/A | % | Post-1950- Assume similar to DOE warehouse reference model Pre-1950s- assume same as post-1950
Skylight U-Value | N/A | Btu/hr-ft²-F (U-Value) | N/A | Btu/hr-ft²-F (U-Value) | N/A | Btu/hr-ft²-F (U-Value) | N/A | Btu/hr-ft²-F (U-Value) | Post-1950- Assume similar to DOE warehouse reference model Pre-1950s- assume same as post-1950
Skylight Solar Heat Gain | N/A | SHGC | N/A | SHGC | N/A | SHGC | N/A | SHGC | Post-1950- Assume similar to DOE warehouse reference model Pre-1950s- assume same as post-1950
Skylight VLT | N/A | % | N/A | % | N/A | % | N/A | % | Post-1950- Assume similar to DOE warehouse reference model Pre-1950s- assume same as post-1950
Local Shading Devices | N/A |  | N/A |  | N/A |  | N/A |  | Post-1950- Assume similar to DOE warehouse reference model Pre-1950s- assume same as post-1950 | External overhangs or awnings 14% Yes | External overhangs or awnings | External overhangs or awnings 12% Yes | External overhangs or awnings 18% Yes
Infiltration / Air Permeability | 1.11 | ACH | 0.74 | ACH | 0.74 | ACH | 0.2 | ACH | Post-1950- Assume similar to DOE warehouse reference model Pre-1950s- Assume 50% increase compared to 1950-1980.
Occupancy
Occupant Density | Space Type | Occupant Density | Space Type | Occupant Density | Space Type | Occupant Density | Space Type | Occupant Density |  | Occupancy (Individual Variables) Number of employees avg: 0.000439453125 per sqft Assembly seating capacity avg: 0.008554216867469879 per sqft | Occupancy (Individual Variables) Number of employees avg: 0.0005114155251141553 per sqft Assembly seating capacity avg: 0.0017241379310344827 per sqft | Occupancy (Individual Variables) Number of employees avg: 0.0002954031650339111 per sqft Assembly seating capacity avg: 3.427071917808219 per sqft | Occupancy (Individual Variables) Number of employees avg: 0.0005914972273567468 per sqft Assembly seating capacity avg: 0.007695099818511797 per sqft
|  | (ft²/person) |  | (ft²/person) |  | (ft²/person) |  | (ft²/person)
| Audience Seating Area | 20 | Audience Seating Area | 20 | Audience Seating Area | 20 | Audience Seating Area | 20 | From COMNET Appendix B
| Atrium | 20 | Atrium | 20 | Atrium | 20 | Atrium | 20 | From COMNET Appendix B
| Basement | 399.8416 | Basement | 399.8416 | Basement | 399.8416 | Basement | 399.8416 | DOE warehouse reference model
| Cafeteria Space | 10 | Cafeteria Space | 10 | Cafeteria Space | 10 | Cafeteria Space | 10 | From COMNET Appendix B
| Conference/Meeting/Multipurpose | 20 | Conference/Meeting/Multipurpose | 20 | Conference/Meeting/Multipurpose | 20 | Conference/Meeting/Multipurpose | 20 | From COMNET Appendix B
Lighting & Receptacles
Interior Lighting Power Density | Space Type | Lighting Power Density | Space Type | Lighting Power Density | Space Type | Lighting Power Density | Space Type | Lighting Power Density |  | Lighting type Incandescent bulbs 57% Yes Fluorescent bulbs 71% Yes Compact fluorescent bulbs 57% Yes Lighting upgrade 57% Yes | Lighting type Light-emitting diode (LED) bulbs 25% Yes Incandescent bulbs 50% Yes Fluorescent bulbs 100% Yes High intensity discharge (HID) bulbs 25% Yes Halogen bulbs 75% Yes Compact fluorescent bulbs 75% Yes Lighting upgrade 25% Yes | Lighting type Light-emitting diode (LED) bulbs 25% Yes Incandescent bulbs 25% Yes Fluorescent bulbs 100% Yes High intensity discharge (HID) bulbs 50% Yes Halogen bulbs 12% Yes Compact fluorescent bulbs 62% Yes Lighting upgrade 25% Yes | Lighting type Light-emitting diode (LED) bulbs 36% Yes Incandescent bulbs 18% Yes Fluorescent bulbs 82% Yes High intensity discharge (HID) bulbs 18% Yes Halogen bulbs 36% Yes Compact fluorescent bulbs 64% Yes Lighting upgrade
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²) | Post-1950s - From COMNET Appendix B; Adjusted by same factors for prior buildings as CBECS Small Office Pre-1950s - CBECS, fluorescent and incandescent bulbs. Assume 30% higher than 1950-1980
| Audience Seating Area | 1.365 | Audience Seating Area | 1.05 | Audience Seating Area | 1.05 | Audience Seating Area | 0.7
| Atrium | 0.39 | Atrium | 0.3 | Atrium | 0.3 | Atrium | 0.2
| Basement | 1 | Basement | 1 | Basement | 1 | Basement | 1 | DOE warehouse reference model
| Cafeteria Space | 1.25 | Cafeteria Space | 1.25 | Cafeteria Space | 1.25 | Cafeteria Space | 0.75
| Conference/Meeting/Multipurpose | 1.25 | Conference/Meeting/Multipurpose | 1.25 | Conference/Meeting/Multipurpose | 1.25 | Conference/Meeting/Multipurpose | 0.75
Daylighting Controls | None |  | None |  | None |  | None |  | Post-1950s - From COMNET Appendix B Pre-1950s - CBECS
Other Lighting Control Credits | None |  | None |  | None |  | None |  | Post-1950s - From COMNET Appendix B Pre-1950s - CBECS | Lighting controls Multi-level lighting or dimming 14% Yes Daylight harvesting 14% Yes Occupancy sensors 14% Yes Light scheduling 14% Yes | Lighting controls Occupancy sensors 75% Yes Light scheduling 50% Yes | Lighting controls Multi-level lighting or dimming 12% Yes Daylight harvesting 12% Yes Occupancy sensors 38% Yes Light scheduling 25% Yes BAS controls lighting 12% Yes | Lighting controls Occupancy sensors 55% Yes Light scheduling 27% Yes | Add some lighting controls? (CBECS)
External / Site Lighting Power (W) | Exterior Lights | 2766 | Exterior Lights | 2766 | Exterior Lights | 2766 | Exterior Lights | 2303 | Assume similar to small office building
Receptacle Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density |  | Plug loads (Individual Variables) Number of closed case refrigeration units avg: 0.00015384615384615385 per sqft Number of computers avg: 0.0010241545893719807 per sqft Number of compact refrigerators avg: 4e-05 per sqft Number of residential refrigerators avg: 5.524861878453039e-05 per sqft Electrical upgrade 29% Yes | Plug loads (Individual Variables) Number of closed case refrigeration units avg: 9.549071618037135e-05 per sqft Number of residential refrigerators avg: 0.00022222222222222223 per sqft Number of computers avg: 0.0008401826484018265 per sqft Number of walk-in units avg: 2.1220159151193635e-05 per sqft Number of open case refrigeration units avg: 0.00011956521739130435 per sqft Electrical upgrade | Plug loads (Individual Variables) Number of ice makers avg: 6.993006993006993e-06 per sqft Number of closed case refrigeration units avg: 7.692307692307693e-05 per sqft Number of refrigerated vending machines avg: 3.076923076923077e-05 per sqft Number of residential refrigerators avg: 0.0001032258064516129 per sqft Number of computers avg: 0.00011410459587955626 per sqft Number of compact refrigerators avg: 8.645533141210375e-05 per sqft Electrical upgrade 12% Yes | Plug loads (Individual Variables) Number of closed case refrigeration units avg: 0.00023391812865497077 per sqft Number of refrigerated vending machines avg: 2.4752475247524754e-05 per sqft Number of residential refrigerators avg: 6.704486848891181e-05 per sqft Number of computers avg: 0.0004162576084822305 per sqft Number of compact refrigerators avg: 7.874015748031496e-05 per sqft Number of walk-in units avg: 5.0632911392405066e-05 per sqft Electrical upgrade
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²)
| Audience Seating Area | 0.5 | Audience Seating Area | 0.5 | Audience Seating Area | 0.5 | Audience Seating Area | 0.5 | From COMNET Appendix B
| Atrium | 0.5 | Atrium | 0.5 | Atrium | 0.5 | Atrium | 0.5 | From COMNET Appendix B
| Basement | 1 | Basement | 1 | Basement | 1 | Basement | 1 | DOE warehouse reference model
| Cafeteria Space | 0.5 | Cafeteria Space | 0.5 | Cafeteria Space | 0.5 | Cafeteria Space | 0.5 | From COMNET Appendix B
| Conference/Meeting/Multipurpose | 0.73 | Conference/Meeting/Multipurpose | 0.73 | Conference/Meeting/Multipurpose | 0.73 | Conference/Meeting/Multipurpose | 0.73 | From COMNET Appendix B
Gas Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²)
| Audience Seating Area | 0 | Audience Seating Area | 0 | Audience Seating Area | 0 | Audience Seating Area | 0 | From COMNET Appendix B
| Atrium | 0 | Atrium | 0 | Atrium | 0 | Atrium | 0 | From COMNET Appendix B
| Basement | 0 | Basement | 0 | Basement | 0 | Basement | 0 | DOE warehouse reference model
| Cafeteria Space | 80 | Cafeteria Space | 90 | Cafeteria Space | 80 | Cafeteria Space | 75 | From COMNET Appendix B
| Conference/Meeting/Multipurpose | 0 | Conference/Meeting/Multipurpose | 0 | Conference/Meeting/Multipurpose | 0 | Conference/Meeting/Multipurpose | 0 | From COMNET Appendix B
Process Loads | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density | Space Type | Equipment Power Density |  | Cooking fuel source Propane used for cooking 29% Yes Electricity used for cooking 14% Yes Process load (Individual Variables) Elevators 43% Yes Number of servers avg: 2.5e-05 per sqft Manufacturing fuel source | Cooking fuel source Propane used for cooking 25% Yes Natural gas used for cooking 25% Yes Process load (Individual Variables) Elevators 50% Yes Number of servers avg: 2.4630541871921184e-05 per sqft Manufacturing fuel source | Cooking fuel source Electricity used for cooking 12% Yes Process load (Individual Variables) Elevators 25% Yes Number of servers avg: 0.00011527377521613833 per sqft Manufacturing fuel source | Cooking fuel source Propane used for cooking 36% Yes Electricity used for cooking 18% Yes Natural gas used for cooking 9% Yes Fuel oil used for cooking 9% Yes Process load (Individual Variables) Elevators 45% Yes Number of servers avg: 0.00013278008298755187 per sqft Manufacturing fuel source
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²)
Refrigeration
Cases | Space, Case | Cooling Capacity | Space, Case | Cooling Capacity | Space, Case | Cooling Capacity | Space, Case | Cooling Capacity
|  | (W) |  | (W) |  | (W) |  | (W)
| Walk-In Freezer | 1678.72 | Walk-In Freezer | 1678.72 | Walk-In Freezer | 1678.72 | Walk-In Freezer | 1678.72 | Based on CBECS for Restaurant |  |  |  |  | Should refrigeration be the same for all vintages?
| Self-Contained Display | 2238.7 | Self-Contained Display | 2238.7 | Self-Contained Display | 2238.7 | Self-Contained Display | 2238.7 | Based on CBECS for Restaurant
Condenser | Condenser Name | Equipment Load | Condenser Name | Equipment Load | Condenser Name | Equipment Load | Condenser Name | Equipment Load
|  | (W/ft²) |  | (W/ft²) |  | (W/ft²) |  | (W/ft²)
| Rack 1 | 330 | Rack 1 | 330 | Rack 1 | 330 | Rack 1 | 330 | Based on CBECS for Restaurant
| Rack 2 | 330 | Rack 2 | 330 | Rack 2 | 330 | Rack 2 | 330 | Based on CBECS for Restaurant
Schedules
Internal Gain Schedules | Space Type | Schedule | Space Type | Schedule | Space Type | Schedule | Space Type | Schedule
| Audience Seating Area | ASSEMBLY_SCH | Audience Seating Area | ASSEMBLY_SCH | Audience Seating Area | ASSEMBLY_SCH | Audience Seating Area | ASSEMBLY_SCH | From COMNET Appendix B, Assembly
| Atrium | ASSEMBLY_SCH | Atrium | ASSEMBLY_SCH | Atrium | ASSEMBLY_SCH | Atrium | ASSEMBLY_SCH | From COMNET Appendix B, Assembly
| Cafeteria Space | REST_SCH | Cafeteria Space | REST_SCH | Cafeteria Space | REST_SCH | Cafeteria Space | REST_SCH | From COMNET Appendix B, Restaurant
| Conference/Meeting/Multipurpose | ASSEMBLY_SCH | Conference/Meeting/Multipurpose | ASSEMBLY_SCH | Conference/Meeting/Multipurpose | ASSEMBLY_SCH | Conference/Meeting/Multipurpose | ASSEMBLY_SCH | From COMNET Appendix B, Assembly
Building Hours of Operation | 9 am to 10 pm most days |  | 9 am to 10 pm most days |  | 9 am to 10 pm most days |  | 9 am to 10 pm most days |  | From COMNET Appendix B, Assembly
HVAC Airside
Primary HVAC System Type - Dominant space type | Packaged central air handling unit with CAV |  | Multizone VAV |  | Multizone VAV |  | Multizone VAV |  | CBECS Large Office Reference Model Pre 1950 - packaged AHU with AC | Heating ventilation type Heating ventilation: None of these 14% Yes Heating ventilation: Central air handling with CAV 14% Yes Cooling ventilation type Cooling ventilation: Dedicated outside air system 14% Yes Cooling ventilation: Central air-handling unit with CAV 29% Yes Cooling ventilation: Demand controlled ventilation 14% Yes Cooling ventilation: Central air-handling unit with VAV 14% Yes Main heating equipment 29% Individual space heaters (other than heat pumps) 43% Boilers inside (or adjacent to) the building that produce steam or hot water 29% Packaged central unit (roof mounted) HVAC equipment upgrade 14% Yes | Heating ventilation type Heating ventilation: Demand controlled ventilation 25% Yes Heating ventilation: Central air handling with CAV 50% Yes Cooling ventilation type Cooling ventilation: Central air-handling unit with CAV 50% Yes Cooling ventilation: Demand controlled ventilation 25% Yes Main heating equipment 50% Individual space heaters (other than heat pumps) 50% District steam or hot water piped in from outside the building HVAC equipment upgrade | Heating ventilation type Heating ventilation: Central air handling with VAV 38% Yes Heating ventilation: Demand controlled ventilation 12% Yes Heating ventilation: Dedicated outside air system 25% Yes Heating ventilation: Central air handling with CAV 12% Yes Cooling ventilation type Cooling ventilation: Dedicated outside air system 12% Yes Cooling ventilation: Central air-handling unit with CAV 25% Yes Cooling ventilation: Demand controlled ventilation 12% Yes Cooling ventilation: Central air-handling unit with VAV 38% Yes Main heating equipment 12% District steam or hot water piped in from outside the building 12% Individual space heaters (other than heat pumps) 12% Boilers inside (or adjacent to) the building that produce steam or hot water 38% Packaged central unit (roof mounted) HVAC equipment upgrade 25% Yes | Heating ventilation type Heating ventilation: None of these 9% Yes Heating ventilation: Central air handling with VAV 18% Yes Heating ventilation: Underfloor air distribution 9% Yes Heating ventilation: Demand controlled ventilation 9% Yes Heating ventilation: Central air handling with CAV 45% Yes Cooling ventilation type Cooling ventilation: Central air-handling unit with CAV 45% Yes Cooling ventilation: Demand controlled ventilation 9% Yes Cooling ventilation: Central air-handling unit with VAV 18% Yes Main heating equipment 18% Individual space heaters (other than heat pumps) 55% Boilers inside (or adjacent to) the building that produce steam or hot water 9% Packaged central unit (roof mounted) 18% Heat pumps (other than components of a packaged unit) HVAC equipment upgrade | Are the post-1950 systems CAV or VAV?
Other HVAC System Type(s) | None |  | None |  | None |  | None
System Parameters and Controls (Economizer, DCV, energy recovery, etc.) | Temperature controlled by programmable thermostat |  | Differential Dry Bulb Economizer |  | Differential Dry Bulb Economizer |  | Differential Dry Bulb Economizer |  | CBECS Large Office Reference Model Pre 1950 CBECCS- programmable thermostat | How reduce cooling 29% Manually change thermostat 14% Manually shut down equipment 14% Part of the Building Automation System Economizer cycle How reduce heating 57% Manually change thermostat 29% Programmable thermostat | How reduce cooling 25% Manually change thermostat 25% Part of the Building Automation System Economizer cycle 50% Yes How reduce heating 25% Manually change thermostat 25% Part of the Building Automation System | How reduce cooling 38% Programmable thermostat Economizer cycle 25% Yes How reduce heating 25% Manually change thermostat 25% Programmable thermostat 12% Part of the Building Automation System | How reduce cooling 27% Part of the Building Automation System 9% Manually change thermostat 9% Programmable thermostat Economizer cycle 27% Yes How reduce heating 27% Part of the Building Automation System 45% Manually change thermostat 27% Programmable thermostat
HVAC Waterside
Cooling Source Parameters | Direct expansion coils in air handling units, COP = 2.70 |  | 2 Chillers, COP = 5.11 |  | 2 Chillers, COP = 5.2 |  | 2 Chillers, COP = 5.5 |  | CBECS Large Office Reference Model Pre 1950 CBECCS- packaged AC, main cooling replaced ASHRAE 90.1 2004- EER = 9.2 for air-cooled AC >760 kBtuh | Main cooling replaced 29% Yes Chiller type Chiller type: Water cooled 14% Yes Chiller type: Air-cooled 14% Yes Cooling fuel source Electricity used for cooling 57% Yes | Main cooling replaced Cooling fuel source District chilled water used for cooling 50% Yes Electricity used for cooling 25% Yes | Main cooling replaced 25% Yes Cooling fuel source Electricity used for cooling 62% Yes | Chiller type Chiller type: Water cooled 9% Yes Chiller type: Air-cooled 9% Yes Cooling fuel source Electricity used for cooling 64% Yes | Should air-cooled or water-cooled chiller be used?
Chilled Water Loop & Pump Parameters | N/A (packaged system) |  | Variable speed pump, 90% efficient |  | Variable speed pump, 90% efficient |  | Variable speed pump, 90% efficient
Condenser Water Loop & Pump Parameters | N/A (packaged system) |  | Constant speed pump, 87% efficient |  | Constant speed pump, 87% efficient |  | Constant speed pump, 87% efficient
Cooling tower Parameters | N/A (packaged system) |  | 2 cooling towers |  | 2 cooling towers |  | 2 cooling towers
Heating Source Parameters | Natural gas fired boiler, 78% efficient |  | Gas boiler, 76% efficient |  | Gas boiler, 70% efficient |  | Gas boiler, 78% efficient |  | Pre 1950 CBECCS- natural gas heating, 73% heating system replaced | Heating fuel source Fuel oil used for main heating 57% Yes Natural gas used for main heating 14% Yes Propane used for main heating 14% Yes Electricity used for main heating 14% Yes Main heating replaced 43% Yes | Heating fuel source District steam used for main heating 50% Yes Electricity used for main heating 25% Yes Wood used for main heating 25% Yes Main heating replaced | Heating fuel source District steam used for main heating 12% Yes Propane used for main heating 12% Yes Fuel oil used for main heating 25% Yes Natural gas used for main heating 25% Yes Main heating replaced 12% Yes | Heating fuel source Fuel oil used for main heating 27% Yes Natural gas used for main heating 9% Yes Propane used for main heating 36% Yes Electricity used for main heating 18% Yes Wood used for main heating 9% Yes | Mix of fuels (CBECS). Pre-1950: About 50% of the heating systems have been replaced (CBECS). Current assumptions represent the unreplaced systems.
Hot Water Loop & Pump Parameters | Steam (no pump) |  | Variable speed pump, 87.5% efficient |  | Variable speed pump, 87.5% efficient |  | Variable speed pump, 87.5% efficient
Service Hot Water
Domestic Hot Water System Parameters | Fuel-oil fired water heater, 65% efficient |  | Gas boiler, 78% efficient, 60C setpoint |  | Gas boiler, 78% efficient, 60C setpoint |  | Gas boiler, 80% efficient, 60C setpoint |  | Pre 1950 CBECCS- fuel oil water heating | DHW fuel source Electricity used for water heating 29% Yes Fuel oil used for water heating 43% Yes Natural gas used for water heating 14% Yes Plumbing system upgrade | DHW fuel source Electricity used for water heating 25% Yes District steam used for water heating 25% Yes Propane used for water heating 25% Yes Fuel oil used for water heating 25% Yes Plumbing system upgrade | Plumbing system upgrade 12% Yes DHW fuel source Natural gas used for water heating 38% Yes Electricity used for water heating 12% Yes Fuel oil used for water heating 12% Yes District steam used for water heating 12% Yes | DHW fuel source Electricity used for water heating 55% Yes Propane used for water heating 18% Yes Fuel oil used for water heating 9% Yes Natural gas used for water heating 18% Yes Plumbing system upgrade | Mix of fuels
Renewable Energy Systems
Renewable Energy System Description and Parameters | N/A |  | N/A |  | N/A |  | N/A |  | Based on CBECS for Restaurant
General Notes
Notes

## Pre-1950 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/person/day) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Audience Seating Area | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 8.9 | 21.188 | 0.25 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.75 | From COMNET Appendix C
Atrium | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 8.9 | 21.188 | 0.25 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.75 | From COMNET Appendix C
Basement | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 0 | 0 | 0.25 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.75 | From COMNET Appendix C
Cafeteria Space | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 21.19 | 21.188 | 0.93 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.75 | From COMNET Appendix C
Conference/Meeting/Multipurpose | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 8.9 | 21.188 | 0.25 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.7 | NaturalGas | 0.75 | From COMNET Appendix C

## 1950-1980 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/person/day) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Audience Seating Area | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 8.9 | 21.188 | 0.25 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.72 | NaturalGas | 0.8
Atrium | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 8.9 | 21.188 | 0.25 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.72 | NaturalGas | 0.8
Basement | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 0 | 0 | 0.25 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.72 | NaturalGas | 0.8
Cafeteria Space | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 21.19 | 21.188 | 0.93 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.72 | NaturalGas | 0.8
Conference/Meeting/Multipurpose | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 8.9 | 21.188 | 0.25 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 5.5 | NaturalGas | HotWaterBoiler | 0.72 | NaturalGas | 0.8

## 1980-2000 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/person/day) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Audience Seating Area | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 8.9 | 21.188 | 0.25 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 6 | NaturalGas | HotWaterBoiler | 0.74 | NaturalGas | 0.8
Atrium | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 8.9 | 21.188 | 0.25 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 6 | NaturalGas | HotWaterBoiler | 0.74 | NaturalGas | 0.8
Basement | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 0 | 0 | 0.25 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 6 | NaturalGas | HotWaterBoiler | 0.74 | NaturalGas | 0.8
Cafeteria Space | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 21.19 | 21.188 | 0.93 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 6 | NaturalGas | HotWaterBoiler | 0.74 | NaturalGas | 0.8
Conference/Meeting/Multipurpose | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 8.9 | 21.188 | 0.25 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 6 | NaturalGas | HotWaterBoiler | 0.74 | NaturalGas | 0.8

## Post-2000 Space Conditioning
Input | Space Conditioning & Ventilation | [26 empty] | Carbon Free Boston
Calculation | [27 empty] | 259104-00
Notes
Zone Types | [27 empty] | Source/Comments
Name | Conditioned | Thermostat Schedule | Heating Setback | Heating Setpoint | Cooling Setpoint | Cooling Setback | Min Relative Humidity | Max Relative Humidity | DHW Demand | Occupant-Based Ventilation | Area-Based Ventilation | Area-Based Exhaust | Minimum Air Change Requirements | Zone Level DCV | DCV Setpoint | HVAC System | HVAC System Heating Coil Type | HVAC Zone Equipment | HVAC Zone Equipment Heating Coil Type | HVAC Plant Condenser Type | HVAC Plant Chiller Type | Cooling COP | HVAC Plant Boiler Fuel | HVAC Plant Boiler Type | Heating Efficiency | Water Heater Fuel | Water Heater Efficiency
| (Y/N) |  | (°F) | (°F) | (°F) | (°F) | (%) | (%) | (gal/person/day) | (cfm/person) | (cfm/ft²) | (cfm/ft²) | (ACH) | (Y/N) | (ppm)
Audience Seating Area | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 8.9 | 21.188 | 0.25 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 6 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8 | From COMNET Appendix C
Atrium | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 8.9 | 21.188 | 0.25 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 6 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8 | From COMNET Appendix C
Basement | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 0 | 0 | 0.25 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 6 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8 | From COMNET Appendix C
Cafeteria Space | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 21.19 | 21.188 | 0.93 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 6 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8 | From COMNET Appendix C
Conference/Meeting/Multipurpose | Y | Setpoint active 8 am to 12 am | 70 | 72 | 78 | 86 | N/A | N/A | 8.9 | 21.188 | 0.25 | 0 | N/A | N | N/A | VAV | HotWater | VAV | HotWater | AirCooled | ElectricCentrifugalChiller | 6 | NaturalGas | HotWaterBoiler | 0.78 | NaturalGas | 0.8 | From COMNET Appendix C

## Pre-1950 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Audience Seating Area | Audience Seating Area | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | COMNET Appendix C, Assembly
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.8 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.1
Occupancy - Cafeteria Space | Cafeteria Space | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2 | COMNET Appendix C, Restaurant
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Occupancy - Atrium | Atrium | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | COMNET Appendix C, Assembly
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.8 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.1
Occupancy - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | COMNET Appendix C, Assembly
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.8 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.1
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Audience Seating Area | Audience Seating Area | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.35 | 0.35 | 0.35 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.05 | 0.05
Lighting - Cafeteria Space | Cafeteria Space | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | COMNET Appendix C, Restaurant
|  | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
|  | Sun/Holiday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
Lighting - Atrium | Atrium | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.35 | 0.35 | 0.35 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.05 | 0.05
Lighting - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.35 | 0.35 | 0.35 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.05 | 0.05
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Audience Seating Area | Audience Seating Area | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.05 | 0.05
Receptacles - Cafeteria Space | Cafeteria Space | Weekday | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03 | COMNET Appendix C, Restaurant
|  | Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
|  | Sun/Holiday | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
Receptacles - Atrium | Atrium | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.25 | 0.05 | COMNET Appendix C, Restaurant
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.05 | 0.05
Receptacles - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.05 | 0.05
Receptacles - |  | Weekday | [24 empty] | COMNET Appendix C, Assembly
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - Audience Seating Area | Audience Seating Area | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.35 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COMNET Appendix C, Assembly
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
Domestic Hot Water - Cafeteria Space | Cafeteria Space | Weekday | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | COMNET Appendix C, Restaurant
|  | Sat | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
|  | Sun/Holiday | 0.25 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Domestic Hot Water - Atrium | Atrium | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.35 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COMNET Appendix C, Assembly
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
Domestic Hot Water - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.35 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COMNET Appendix C, Assembly
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Audience Seating Area | Audience Seating Area | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | COMNET Appendix C, Assembly
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - Cafeteria Space | Cafeteria Space | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | COMNET Appendix C, Restaurant
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - Atrium | Atrium | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | COMNET Appendix C, Assembly
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | COMNET Appendix C, Assembly
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - |  | Weekday
Sat
Sun/Holiday

## 1950-1980 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Audience Seating Area | Audience Seating Area | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | COMNET Appendix C, Assembly
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.8 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.1
Occupancy - Cafeteria Space | Cafeteria Space | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2 | COMNET Appendix C, Restaurant
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Occupancy - Atrium | Atrium | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | COMNET Appendix C, Assembly
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.8 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.1
Occupancy - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | COMNET Appendix C, Assembly
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.8 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.1
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Audience Seating Area | Audience Seating Area | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.35 | 0.35 | 0.35 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.05 | 0.05
Lighting - Cafeteria Space | Cafeteria Space | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | COMNET Appendix C, Restaurant
|  | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
|  | Sun/Holiday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
Lighting - Atrium | Atrium | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.35 | 0.35 | 0.35 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.05 | 0.05
Lighting - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.35 | 0.35 | 0.35 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.05 | 0.05
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Audience Seating Area | Audience Seating Area | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.05 | 0.05
Receptacles - Cafeteria Space | Cafeteria Space | Weekday | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03 | COMNET Appendix C, Restaurant
|  | Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
|  | Sun/Holiday | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
Receptacles - Atrium | Atrium | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.25 | 0.05 | COMNET Appendix C, Restaurant
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.05 | 0.05
Receptacles - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.05 | 0.05
Receptacles - |  | Weekday | [24 empty] | COMNET Appendix C, Assembly
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - Audience Seating Area | Audience Seating Area | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.35 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COMNET Appendix C, Assembly
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
Domestic Hot Water - Cafeteria Space | Cafeteria Space | Weekday | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | COMNET Appendix C, Restaurant
|  | Sat | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
|  | Sun/Holiday | 0.25 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Domestic Hot Water - Atrium | Atrium | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.35 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COMNET Appendix C, Assembly
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
Domestic Hot Water - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.35 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COMNET Appendix C, Assembly
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Audience Seating Area | Audience Seating Area | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | COMNET Appendix C, Assembly
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - Cafeteria Space | Cafeteria Space | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | COMNET Appendix C, Restaurant
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - Atrium | Atrium | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | COMNET Appendix C, Assembly
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | COMNET Appendix C, Assembly
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - |  | Weekday
Sat
Sun/Holiday

## 1980-2000 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Audience Seating Area | Audience Seating Area | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | COMNET Appendix C, Assembly
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.8 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.1
Occupancy - Cafeteria Space | Cafeteria Space | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2 | COMNET Appendix C, Restaurant
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Occupancy - Atrium | Atrium | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | COMNET Appendix C, Assembly
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.8 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.1
Occupancy - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | COMNET Appendix C, Assembly
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.8 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.1
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Audience Seating Area | Audience Seating Area | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.35 | 0.35 | 0.35 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.05 | 0.05
Lighting - Cafeteria Space | Cafeteria Space | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | COMNET Appendix C, Restaurant
|  | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
|  | Sun/Holiday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
Lighting - Atrium | Atrium | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.35 | 0.35 | 0.35 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.05 | 0.05
Lighting - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.35 | 0.35 | 0.35 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.05 | 0.05
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Audience Seating Area | Audience Seating Area | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.05 | 0.05
Receptacles - Cafeteria Space | Cafeteria Space | Weekday | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03 | COMNET Appendix C, Restaurant
|  | Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
|  | Sun/Holiday | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
Receptacles - Atrium | Atrium | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.25 | 0.05 | COMNET Appendix C, Restaurant
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.05 | 0.05
Receptacles - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.05 | 0.05
Receptacles - |  | Weekday | [24 empty] | COMNET Appendix C, Assembly
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - Audience Seating Area | Audience Seating Area | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.35 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COMNET Appendix C, Assembly
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
Domestic Hot Water - Cafeteria Space | Cafeteria Space | Weekday | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | COMNET Appendix C, Restaurant
|  | Sat | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
|  | Sun/Holiday | 0.25 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Domestic Hot Water - Atrium | Atrium | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.35 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COMNET Appendix C, Assembly
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
Domestic Hot Water - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.35 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COMNET Appendix C, Assembly
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Audience Seating Area | Audience Seating Area | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | COMNET Appendix C, Assembly
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - Cafeteria Space | Cafeteria Space | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | COMNET Appendix C, Restaurant
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - Atrium | Atrium | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | COMNET Appendix C, Assembly
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | COMNET Appendix C, Assembly
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - |  | Weekday
Sat
Sun/Holiday

## Post-2000 Schedules
Input | Schedules (optional) | [25 empty] | Carbon Free Boston
Calculation | [26 empty] | 259104-00
Notes
Occupancy | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Occupancy - Audience Seating Area | Audience Seating Area | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | COMNET Appendix C, Assembly
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.8 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.1
Occupancy - Cafeteria Space | Cafeteria Space | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2 | COMNET Appendix C, Restaurant
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Occupancy - Atrium | Atrium | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | COMNET Appendix C, Assembly
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.8 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.1
Occupancy - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | COMNET Appendix C, Assembly
|  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.8 | 0.1 | 0.1
|  | Sun/Holiday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.1
Occupancy - |  | Weekday
Sat
Sun/Holiday
Lighting | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Lighting - Audience Seating Area | Audience Seating Area | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.35 | 0.35 | 0.35 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.05 | 0.05
Lighting - Cafeteria Space | Cafeteria Space | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | COMNET Appendix C, Restaurant
|  | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
|  | Sun/Holiday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
Lighting - Atrium | Atrium | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.35 | 0.35 | 0.35 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.05 | 0.05
Lighting - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.35 | 0.35 | 0.35 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.05 | 0.05
Lighting - |  | Weekday
Sat
Sun/Holiday
Receptacles | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Receptacles - Audience Seating Area | Audience Seating Area | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.05 | 0.05
Receptacles - Cafeteria Space | Cafeteria Space | Weekday | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03 | COMNET Appendix C, Restaurant
|  | Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
|  | Sun/Holiday | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
Receptacles - Atrium | Atrium | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.25 | 0.05 | COMNET Appendix C, Restaurant
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.05 | 0.05
Receptacles - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.25 | 0.05 | COMNET Appendix C, Assembly
|  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05
|  | Sun/Holiday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.05 | 0.05
Receptacles - |  | Weekday | [24 empty] | COMNET Appendix C, Assembly
Sat
Sun/Holiday
Receptacles - |  | Weekday
Sat
Sun/Holiday
Domestic Hot Water | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Domestic Hot Water - Audience Seating Area | Audience Seating Area | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.35 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COMNET Appendix C, Assembly
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
Domestic Hot Water - Cafeteria Space | Cafeteria Space | Weekday | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | COMNET Appendix C, Restaurant
|  | Sat | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
|  | Sun/Holiday | 0.25 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Domestic Hot Water - Atrium | Atrium | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.35 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COMNET Appendix C, Assembly
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
Domestic Hot Water - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.35 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COMNET Appendix C, Assembly
|  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
|  | Sun/Holiday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
Domestic Hot Water - |  | Weekday
Sat
Sun/Holiday
Process Loads | [26 empty] | Source/Comments
| Schedule | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
Process Loads - Audience Seating Area | Audience Seating Area | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | COMNET Appendix C, Assembly
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - Cafeteria Space | Cafeteria Space | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | COMNET Appendix C, Restaurant
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - Atrium | Atrium | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | COMNET Appendix C, Assembly
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | COMNET Appendix C, Assembly
|  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun/Holiday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Process Loads - |  | Weekday
Sat
Sun/Holiday

## Review
Input | Review |  |  |  | Carbon Free Boston |  | Notes:
Calculation |  |  |  |  | 259104-00 |  | - Create a copy of the Review tab for each model review
Notes | [6 empty] | - The reviewer should review the model itself, and not rely on what is documented in the Calc Plan
[5 empty] | Modeller | Reviewer
Reviewed by:
Date of review:
Review type:
Project Information (section to be filled out by modeller prior to review)
Project phase & modelling protocol: | Example: 100% Design Development, ASHRAE 90.1-2010 proposed and baseline model
Link to archived model file:
Link to zoning diagram:
Link to relevant drawing set:
Link to current results:
Link to energy model report:
Self-review of model is complete (Column G) |  | If "No", please indicate why self-review has not been performed:
Questions for reviewer and/or comments about model
Model Metrics | Proposed | Baseline | Benchmark (if known) | Units
Energy Use Intensity (EUI) |  |  |  | kBtu/ft²/year
Heating Plant Capacity |  |  |  | Btu/ft²
Cooling Plant Capacity |  |  |  | ft²/ton
Total Design Supply Airflow |  |  |  | cfm/ft²
Total Outdoor Airflow |  |  |  | cfm/ft²
Documentation and file storage
Inputs documented in this workbook or elsewhere
Files archived and saved in appropriate location on network
Detailed calculations (in support of input values) are documented and saved
Comments
Weather
Appropriate and correct weather file is used. A copy is saved on the network in the "Weather Data" folder.
Climate zone is correct for project location
Appropriate and correct Design Day data is used (check against Basis of Design report)
Comments
Geometry and Shading
Building compass orientation is correct
Building elevation above sea level is correct
Overhangs and/or other shading devices, or site shading, if modelled, are correctly configured in the software
Comments
Zoning
The number of zones in the model is appropriate for the desired level of analysis. Rooms of a similar type and internal load density with the same exposure may be zoned together.
Zoning is the same between model variants, unless variation is justified by an evaluated measure
Comments
Envelope and Construction
Window to gross wall ratio seems reasonable for the building and matches design drawings
Construction types are correctly assigned to proposed and baseline models
Window U-values, SHGC/G-values, and VLT are whole-assembly values (including framing impacts) and are input as required by the software
Opaque U-values are whole-assembly values and are input as required by the software. Insulation values of steel or wood-framed walls are appropriately de-rated in accordance with ASHRAE Appendix A or other reference standard.
U-values of horizontal constructions and glazing are derated for horizontal convection (U-values should be worse than vertical assemblies)
For natural ventilation models: window opening sizes, opening positions and the ventilation methodology are correct
Model accounts for an appropriate level of thermal mass. (Check that construction layer build-up reasonably matches design, or room mass settings are appropriate for the building construction type.)
Modelled infiltration rates are reasonable and identical between model variants, unless modification is justified for a measure evaluation
Comments
Internal Loads
Interior lighting power densities are reasonable given the building use(s)
Decorative lighting is accounted for in lighting power density values or separately, as appropriate
Daylight control is included where appropriate
Credit is taken for reduced lighting power due to occupancy sensors where appropriate
Receptacle loads and occupant densities are the same for all model variants, unless modification is justified for a measure evaluation
Peak and scheduled equipment loads represent anticipated actual draws from the equipment rather than nameplate values
Electrical room: entire building switchgear capacity is not assigned as an electric load
Comments
Schedules
Schedules are the same for all model variants, unless modification is justified for a measure evaluation
Internal load schedules set the load to 100% on for the cooling design condition and 100% off for the heating design condition
Internal gain schedules vary throughout the day appropriately
Schedules used are reasonable (i.e. taken from a reference standard, and/or informed by conversation with building owner)
Any continuous loads have an appropriate schedule applied (e.g. escalators, process equipment)
Elevator schedule is included, if applicable
Exterior lighting schedule or photocell control is included, if applicable
Comments
Space Conditioning
All conditioned zones are assigned to HVAC systems
Any included unconditioned zones are set to be unconditioned in the model
Thermostat setpoints and driftpoints are correct
Comments
Airside Systems
Airside systems reasonably approximate the designed systems
Supply air temperatures and control strategies (e.g. SAT reset, economizer control) match the proposed design and baseline requirements
System schedules are consistent with design (e.g. fan schedules align with occupancy schedules such that the HVAC systems are enabled during occupied hours)
Ventilation is included per the design intent. Ventilation rates meet applicable codes.
Ventilation design flow rates and schedules are identical between model variants unless modification is justified
Exhaust is properly accounted for within the capabilities of the software tool. Room exhaust is distinguished from system level exhaust.
Schedules set the ventilation flows to 100% for the heating and cooling design conditions
Ventilation is scheduled ON during occupied hours and OFF during unoccupied hours, or otherwise according to the design sequence of operation
Demand controlled ventilation is modelled if applicable
Proposed fan power is correctly modelled per the design brake horsepowers and motor efficiencies. Baseline fan power includes any applicable pressure drop adjustments. Any included return and exhaust fan power is accounted for.
Fan drives are modelled correctly as either variable or constant speed
Pressure drop across heat recovery devices is accounted for (and not double counted)
Comments
Waterside Systems and Plant Equipment
Equipment types and efficiencies match the proposed design and baseline requirements
Part-load curves are based on actual equipment data or reasonably approximate part-load performance
Capacity of heating and cooling plants is reasonable (check SF/capacity)
Pumps and heat rejection fans are modelled correctly as either variable or constant speed
Control of the plant equipment in the model reasonably approximates the design sequence of operations (e.g. boiler and chiller staging, loop temperatures and reset controls)
If packaged equipment is used, efficiencies of equipment are broken out into supply fan, condenser fan, and compressor
Domestic hot water has been included for both models, as appropriate
Comments
Utility Rates
Rates are included. They are the same for all model variants, unless modification is justified
If Peak and Off-Peak rates apply, they are correctly implemented
Utility rates change often. Documentation of the utility rate(s) used for the analysis has been saved with the model files.
Comments
Metrics Checks
Building predicted annual energy costs are reasonable
Building EUI (Energy Use Index, energy use per square foot) is relatively close to benchmarks for your building type. Refer to the BEM Toolkit for sources of benchmarking data.
Annual cooling and heating load profiles make sense
The HVAC systems effectively satisfy the building loads (i.e. any "unmet" load hours are acceptable for the analysis). If high unmet loads occur, investigate and revise the model to resolve any problems
Comments
Energy Results by End Use
Differences in energy used by end use category between model variants can be explained by actual measures
Fan and pump power differences between model variants are roughly proportional to cooling and heating differences
Correct and consistent units are used when reporting the energy results
Energy uses which should be the same between variant models (e.g. plug loads) are indeed the same
Percentage of energy used by various end uses is reasonable given the building use(s)
Comments
Review Close-Out
Do the results of the energy model make sense according to experiential expertise, engineering judgment, and rules of thumb? If not, review the results again after the modeller has addressed the review comments.
Comments
LEED Specific Review Items
LEED Minimum Energy Performance Calculator is complete and highlighted comments on the Performance Outputs tab have been addressed.
Modelled floor area and space types are consistent with information reported in PIf3: Occupant and Usage Data.
Modelled system parameters align with the mechanical schedules provided for PIf4: Schedule and Overview Documents.
Modelled outdoor airflow is consistent with design OA reported in IEQp1 62.1 Calculator and AHU schedules.
Outdoor air is modelled per the design in the proposed, and per Appendix G requirements in the baseline.
Whenever credit is taken for demand control ventilation in the Proposed Case, the outside air ventilation rates for the Baseline Case are modelled using minimum ASHRAE 62.1 rates.
Any exceptional calculations have been documented in the LEED Minimum Energy Performance Calculator and a supplemental detailed narrative has been provided.
Any LEED CIRs related to the project have been clearly referenced in the documentation.
Core & shell projects: Model follows LEED C&S Appendices guidance. All unfinished spaces are included and modelled identically in the baseline and proposed, unless tenant lease agreement requires improvement over baseline requirements.
Utility rates are sourced from the same place (either EIA rates or actual utility rates for the project).
District energy systems are modelled per the guidance in the reference manual (v4) or the Treatment of District and Campus Thermal Energy In LEED (v2009).
Tilted surfaces are correctly modelled as walls or roofs as defined by ASHRAE 90.1 (per 90.1-2010, roofs are horizontal or tilted at an angle of less than 60° from horizontal).
Answer Options
Yes
No
Unclear
N/A
Review Type
Condensed
Detailed
Note on B10: Condensed reviews are recommended for earlier project phases. Detailed reviews are recommended for later project phases and/or review of a beginner energy modeler's work.